## Specifications
Creation Date: | 2011-01-28 | Authors: | Mark St. Germain / Richard Unkel | Phone Nos.: | (860) 258-4619 / (203) 752-0113
The Department is responsible for the construction and rehabilitation of multiple transportation related facilities throughout the state. These facilities fall under the general term of “vertical construction,” as they have more in common with buildings than roadways. Some typical examples of vertical construction projects administered by the Department would be: • Airport Facilities (Terminals, Hangers) • Railroad Stations • Railroad Repair Shops and Administrative Buildings • Parking Garages • Bus Facilities • Roadway Maintenance Garages • Salt Sheds • Piers and docks Unit Responsibilities: The successful completion of a vertical construction project requires close coordination and cooperation between several Departmental Units and outside agencies, each with their own unique responsibilities • Construction: District personnel are responsible to provide Contract Inspection and Administration. During construction, they coordinate with other DOT units, the Contractor and outside agencies. The District processes all correspondence, holds meetings and teleconferences, verifies compliance with Contract Specifications and Requirements, arranges code inspections and maintains Project Records in accordance with established Departmental Standards. • Facilities Design: The designer of record (if in-house design) or liaison to designer (if outside consultant.) They are responsible for responding to Requests for Information (RFI’s), resolving design related construction issues by providing clarification or interpretation of Contract Documents, issuing Changes Orders (CO’s) and Field Design Changes (FDC’s) as required and attending meetings to monitor and resolve design issues. • Properties and Facilities: Provide required code inspections in accordance with governing building and fire codes. Provide clarifications and interpretations of codes as they relate to the Project. Ultimately, responsible for the issuance of a Certificate of Substantial Completion, allowing occupancy of the facility, as well as the Certificate of Compliance, accepting the Project. • Owner: The facilities constructed are generally owned by the State, however, the end-user may be a different entity. • Outside Agencies: • Department of Public Safety: Building officials from the Department of Public Safety are responsible to perform inspections on threshold buildings, conveying systems (elevators, escalators, etc.) and boilers. They also provide interpretations of building codes (if requested). Office of the State Fire Marshal for Life Safety Inspections. Construction Specification Institute (CSI) Items: Vertical construction projects consist of standard and special provisions items, including as a special provision, a “Major Lump Sum Item” (MLSI). The MLSI is typically assigned a name such as Rail Facility, Bus Facility Upgrade, or Maintenance Facility and includes all the Construction Specification Institute (CSI) items in the Contract. Typically, the MLSI includes all work within a perimeter five feet outside of the building footprint. CSI categorizes the individual components of building trades into distinct divisions, with specific sections in each division. • Division 01 – General Requirements • Division 02 – Existing Conditions • Division 03 – Concrete • Division 04 – Masonry • Division 05 – Metals • Division 06 – Wood, Plastics and Composites • Division 07 – Thermal and Moisture Protection • Division 08 – Openings • Division 09 – Finishes • Division 10 – Specialties • Division 11 – Equipment • Division 12 – Furnishings • Division 13 – Special Construction • Division 14 – Conveying Equipment • Division 21 – Fire Suppression • Division 22 – Plumbing • Division 23 – Heating, Ventilating and Air Conditioning • Division 26 – Electrical • Division 27 – Communications • Division 28 – Electronic Safety and Security • Division 31 – Earthwork • Division 32 – Exterior Improvements • Division 33 – Utilities NOTE: Division 1 – General Requirements: This division is not included in DOT CSI Projects; Section 1.20 of the Standard Specifications 816 is used. Project Start Up: Once the Contract is Awarded, the Contractor must submit a “Schedule of Values.” This schedule associates a dollar amount for each CSI section of the Contract. The values submitted are to be an approximate representation of the value of the work, but are not to be used as the basis for a credit if work is eliminated. The schedule of values total must equal the amount of MLSI. Contractor has to supply a baseline Bar Chart Construction Schedule. Review and approve Schedule of Values and Baseline Schedule. Payment Estimates: At the conclusion of each payment estimate period, the Contractor is required to submit an American Institute of Architects (AIA) Form G702, “Application and Certificate for Payment” and AIA Form G703,“Continuation Sheet” . The Chief Inspector reviews the draft requisition prepared by the Contractor, makes any corrections or alterations, and once satisfied, returns a copy to the Contractor. The Contractor then submits a final, notarized version, based on the approved draft. The Project Engineer then signs the front sheet of the (AIA) Form G702 in the Architect’s Certificate for Payment block lower right corner. The final Forms G702 and G703 become the basis of payment for the MLSI. The final AIA Forms G702 and G703, along with the “AIA Certification Statement” and a copy of the annotated draft requisition are to be kept in the Volume 3 with a Payment Summary Sheet for the MLSI. Review AIA, sign and put in Volume 3. Testing: Submittals (shop drawings, product data, product samples, catalog cuts and quality assurance submittals) for items that are not part of the Standard Specifications are submitted by the Contractor to the Designer/Architect for review and will be returned as either ‘Conforms’, ‘Conforms as Noted’, ‘Revise and Resubmit’, ‘Rejected’, or ‘No Action Required’. All remaining items are tested in accordance with established policies (i.e., concrete, HMA, subbase, etc.) in accordance with the Minimum Schedule for Sampling Materials for Test. The field inspector is then required to verify that the material installed matches the acceptable submittal. A submittal log will be kept as part of the project records. A Final Material Certification provided by the Division Chief of Research and Materials will be required for any projects with FHWA funding or any roadway projects. A request for a Material Certificate will be sent to the DMT from the District which will include information on all the items accepted by the Designer/Architect with a statement indicating the applicable materials conformed to the Contract so that the materials can be excluded from the testing deficiency list. To assist the field inspector the following statement will be incorporated into Site Manager for materials covered by an approved submittal: “No Request for Test Required.” A Final Material Certification will not be provided by the DMT for facilities (vertical)/non-roadway projects, this information will be retained by the DMT “for information only purposes.” Field Design Change’s (FDC’s) and Request for Information (RFI’s): Request for Information (RFI) - Is a request for clarification of the contract documents. This can include clarification of intent of information shown on the plans or in the specifications, requests for information missing from contract documents and interpretation of conflicting information shown on the plans or in the specifications. Procedure for RFI- The Prime Contractor sends the RFI to the Project Staff/District Field Office. If the RFI cannot be resolved by the District Staff the RFI is sent to the Designer for resolution. The Designer prepares a response addressed to the District and the District responds to the Contractor. A response to an RFI should be within 7 days. Request for Change (RFC) - This includes all requests by the Contractor to substitute materials specified in the contract documents. This also includes requests to change the methods of construction as detailed in the contract documents. Before any RFC by the Contractor will be considered, a formal written request from the Contractor must be made to the District and written approval secured before any change in the design will be sanctioned. Procedure for RFC - The Prime Contractor sends a written request to the District’s ADE. The District determines the appropriate parties for review. If design review is required, the request will be sent to the appropriate Project Manager in Design. Design will forward the request, if required to the Consultant Designer for their comment and/or recommendations. Design will forward their recommendation to the District after reviewing the request and/or the Consultant Designer recommendations. The District will make the final decision and approve or not approve the request. A written response of the decision will be sent to the Contractor. A response to an RFC should be within 30 days. Keep a log of RFI’s and RFC’s as part of Project records. Project Meetings: Typically one major project progress meeting is held once a month with all parties involved. Monthly update schedule should be reviewed. Weekly meetings with the Contractor and Field Staff are also held. Contractor has to submit two week look ahead schedules at weekly meetings. Code Inspections: The contractor shall provide the Code Official at least a 3 day notice to schedule the required code inspection and witness of testing.

## Facilities Construction
Revision Date: |  |  | 2011-03-03 | Authors: | Mark St. Germain / Richard Unkel | Phone Nos.: | (860) 258-4619 / (203) 752-0113
Prepared by:
Comments
Footing inspection Prior to Concrete Placement (Sections 1704.4, 109.3.1)
Prepare fill / controlled structural fill, is site prepared per approved report and is placement of fill material compliant. (Section 1803.5)
Approved set of footing and foundation plans plus soil boring and sampling records shall be available at all times. (Section 106.3.1)
Compaction testing reported. (Section 1803.5)
Testing of concrete scheduled by an approved testing agency. (Sections 1704.4, 1905.6)
Foundation Inspection Prior to Concrete Placement (Section 1704.4)
Reinforcing steel. (Sections 1704.4, 1907.0)
Inserts, penetrations, appurtenances and anchoring. (Sections 1604.8, 1704.4)
Forms placed and oiled. (Section 1905.7)
Testing of concrete scheduled by an approved testing agency. (Sections 1704.4, 1905.6)
Temporary Heat (inspected by Code Official) and Cold Weather Protection. (Sections 1905.12, 1905.13, 1905.11.1)
Damp proofing, Waterproofing and Subsoil Drainage System. (Section 1807.0)
Floor Inspection Prior to Concrete Placement
Compaction Testing reported. (Section 1803.5)
Approved set of building plans to be available at the site. (Section 106.3.1)
Perimeter insulation, vapor barrier and isolation of columns. (Section 1911.0)
Reinforcing steel, mesh and haunch placement. (Sections 1905.7, 1907.0)
Slab thickness, construction joints and expansion joints. (Sections 1909.3, 1911.0)
Testing of concrete scheduled by an approved testing agency. (Sections 1704.4, 1905.6)
Underground Inspection of Mechanical, Plumbing, Electrical & Fire Protection (IMC 107.1, IPC 107.1)
Mechanical and Plumbing (IMC 107, IPC 107)
Trench pitch and bedding. (IPC 306.0)
Piping installation and pressure test(s). (IPC 305, 312, 702, 704, IMC 1304, 1209.2)
Backfill material and placement. (IPC 306.3)
Electrical (Sections 2701, 2702, NEC 2005)
Trenching and bedding. (NEC 300.5)
Conduit installation. (NEC 300.5)
Backfill material and placement. (NEC 300.5)
Electrical Service Entrance and Temporary Construction Electrical Service (NEC 590.4(A), 230.0
These services shall be inspected by the Code Official and released to the respective electrical utility company for activation. Sign-off by Code Official is required by the Utility Companies.
Fire Protection - Underground work including fire service and thrust blocking. (NFPA 13 - 2002, Chapter 10, 10.8.2 (thrust blocks))
Trenching and bedding. (NFPA 13 - 2002, 10.4 – 10.9)
Piping installation and pressure test(s). (NFPA 13 – 2002, 10.10.1 – 10.10.2.24)
Backfill material and placement. (NFPA 13 – 2002, 10.9)
Fuel Storage Tank(s) Underground (UST) and Aboveground (AST) Installation (IMC 1301.2, CT Flammable & Combustible Liquids Code, NFPA 30 – 2002 Ch. 2 & 3, CT Oil Burning Equip. Code, NFPA 31 – 2002 Ch. 2 & 3, CT Gas Equipment & Piping Code, NFPA 54 – 2002 Ch. 2, 3, 4, CT LP Gas & LN Gas Code, NFPA 58 – 2002, Ch. 2, 3, 5)
Witness of all manufacturers’ required procedures.
Hold down structures
Backfill material and placement.
Piping and appurtenances and testing.
Structural Steel & Metal Framing Inspection Prior to Concealment
Inspection shall be performed by Special Inspector or Code Official if Special Inspector is not required.
Protection of steel by approved methods prior to masonry. (Section 2203.2)
Floor, roof and wall members, panels, columns, bracing, bolts, washers and welds. (Sections 1704.3, 1704.3.1.2, 1704.3.3)
Spray applied fire resistive material. (Section 1704.11)
Third party reports: prefab steel, assemblies, markings, certified test reports, ASTM, weld filler.
Fabricator Certification / Quality Control Procedures. (Sections 1704.2, 1704.2.1, 1704.2.2)
Masonry & Stone Inspection Prior to Concealment (Sections 1704.5, 2104.1)
Anchor ties. (Sections 1704.5, 2104.1.3, 2109.7)
Lintel and bond courses. (Sections 1704.5, 2104.1.5, 2109.6)
Horizontal and vertical reinforcement. (Sections 1704.5, 2109.6)
Certification of block, brick and accessories. (Section 1704.5)
Mortar type material, temperature and method of application. (Sections 1704.5, 2104.3)
Flashing, dampproofing, weeping, wicking, insulation and penetrations. (Section 1704.5)
Third party reports, prefab masonry units, assemblies, markings, certified test reports and ACI Standards. (Section 1704.5)
Temporary Heat and Cold Weather Protection (Sections 1704.5, 2104.3.3)
Wood Construction Roughing Inspection
Fabricator Certification / Quality Control Procedures. (Sections 1704.6, 2303.0)
Material Grading. (Section 2303.1.1
Connections. (Section 2304.9)
Framing and Details. (Sections 2304.3, 2304.4)
Roof and Floor Diaphragms, Interior and Exterior Shear Walls. (Sections 2305.2, 2305.3)
Construction Cast-In-Place Concrete, Pre-Cast Concrete, Exterior Insulation & Finish Systems (EIFS), Structural Insulated Panel Systems, Curtain Wall Systems and all Special Cases (Sections 1903, 1704.4, 3101.1),Mechanical, Plumbing, Electrical & Fire Protection (including Sprinkler Standpipe, Hood Extinguishing, Detection and Fire Alarm) Above Slab / Rough-In Inspection Prior to Concealment
Rough-in inspections shall be made after the roof, framing, fireblocking, firestopping, draftstopping and bracing is in place and all ducting and other components to be concealed are complete, all sanitary, storm, fire protection and water distribution piping is roughed-in & prior to the installation of wall and ceiling coverings.
Inspections of MEP & FP work shall also include inspection of fire safing, sleeving, sealants, penetrations & thru-penetration firestop systems as well as seismic bracing and attachment (which may be a part of Special Inspection duties)
Mechanical and Plumbing (Sections 2801.1, 2901.1, IMC 107(2))
Piping and duct system installations. (IMC 304, 603, 1107, 1208.1, 1304, 1305, IPC Ch. 6 & 704)
Duct and piping support, hanger systems and seismic bracing. (IMC 304, 305, 603, IPC 308, 1621)
Fire and smoke dampers. (IMC 716.1, 716.3, 716.5, UL 555, NFPA 90A – 2002)
Pipe / duct insulation, identification, valve tags and vibration isolation. (IMC 301.10, 604, 1204, IPC 303, 505, Ch. 6, 719.7)
Witness piping system (domestic water, drain-waste-vent, storm, fuel) testing. (IMC 107.2, 1208, 1209.2, 1304.1, IPC 312)
Witness refrigerant system test and certification provided. (IMC 1108)
Electrical (NEC 2701.0)
Rough-in inspection shall include but not be limited to:
General requirements for electrical installations, conduit and feeder installation. (NEC Art. 110)
Bonding and grounding of devices, boxes, conduit, equipment and structure. (NEC Art. 250)
Service entrance and switchgear installation. (NEC 110.34F, 230, 338, 490 III)
Fire Protection
Rough-in inspection shall include but not be limited to:
Piping system installation. (Section 903.0, NFPA 13)
Hanger systems and seismic bracing. (Section 903.0, NFPA 13)
Witness hydrostatic pressure system test. (Section 903.0, NFPA 13)
General Inspection (Sections 109.3, 705.0, 706.0, 708.0, 709.0)
This section shall also be done on fire walls, fire and smoke barriers constructed in accordance with referenced test assemblies.
Inspections & Testing Prior to Certificate of Compliance and Occupancy (Sections 109.0, 110.0)
Outstanding inspection report violation findings and code discrepancies resolved. (Sections 109.3.10, 113.0)
Outstanding Plan Review report comments and code discrepancies resolved. (Sections 109.3.10, 113.0)
Testing of the emergency power and standby power systems - witnessed by CA & Engineer of Record. (Sections 2702, NEC 700.4, NFPA 110 – 2002)
Testing of fire protection systems. (sprinkler, standpipe, hood and special extinguishing, fire pump, detection & fire alarm systems), special locking area of refuge communication system, emergency lighting and exit signage witnessed by Code Official. (Sections Ch. 9, 1011, 1024, NEC 700, 760, 1021.4)
State of Conn. Dept. of Public Safety - Boiler Bureau inspection, testing & operating certificate (860) 685-8320 where applicable. (CT General Statute Chapter 540)
State of Conn. Dept. of Public Safety - Elevator Bureau inspection, testing & operating certificate. (860) 685-8340. (Section 3001.1.1)
State of Conn. Dept. of Public Health (DPH) approval of sewer, septic and water supply (potability test per IPC 610) Kitchen / food service per Local or Regional Health Department.
State of Conn. Dept. of Environmental Protection registration of fuel oil, motor and aviation fuel and hazardous materials, Engineer of Record to complete required form for CTDOT to sign.
Backflow prevention acceptance by water supplier. (IPC 608)
Certification of HVAC operation and balancing. (IMC 107.2)
Testing of smoke control system - witnessed by Code Official & Engineer of Record. (Section 909.3)
Electrical Ground Fault Protection system performance test, witnessed by Code Official. (NEC 230.95C)
Kitchen Hood exhaust system, laboratory hood and special exhaust system inspection and testing by certified installer / tester, and witnessed by the Code Official. (IMC 507, 510, NFPA 45)
Explosion Hazard Protection Inspection by Engineer of Record. (Section 414)
Inspection of accessible components by Code Official and Engineer of Record. (Chapter 11)