## IMS
|  | Revision Date: | 2011-03-03 | Author: | Anthony Kwentoh | Phone No.: | (860) 594-2673
Prepared by:
Comments
IMS Installation General Requirements:
Review the project plans and special provisions to familiarize with the scope of work and details of the various electrical and electronic components of the system.
Review Notice to Contractor special provisions “Existing IMS” and “IMS Installation” for additional information on the Incident Management System. The IMS shall remain in operation at all times.
Familiarize with the contractor’s work sequence and the contract M&PT plans. It is imperative to monitor the safety of the traveling public during installation of Freeway IMS.
Review contractor’s schedules to track progress and deviations.
Track status ofsubmittals, procurement of materials and timely deliveries to jobsite.
Ensure that all subsurface utilities have been marked out using the “CALL BEFORE YOU DIG – (800)922-4455” prior to any excavation.
Ensure compliance with the applicable permit requirements, and E&S Controls.
Check to ensure contractor complies with all requirements for excavation in Areas of Environmental Concerns (AOEC) per plans and specifications.
Monitor long lead items in correlation to the scheduled milestones such as Camera Lowering Device Poles, Traffic Flow Monitor Detector Poles and Variable Message Signs (VMS) and VMS Structures.
Conduits Installation:
All conduits used shall be the approved types and size per contract plans and specs with proper identification mark and label.
Review trench excavation for correct depth and width per plans. Maintain the minimum depth below the frost line (36” typical).
Verify that conduits are installed at correct depth and pitch. Conduits exiting pull box structures should be installed at a slightly higher elevation to prevent water from entering the conduit system. Also, follow the plan details for conduits crossing at existing utility, under roadway, and other applicable installations.
Verify that multiple conduits in a common trench have proper spacer and support chairs.
In trench, conduits should be spaced with 12” of fill material between multiple conduits.
Ensure that directional bored or jacked conduits under roadway and ramp crossings does not damage the existing pavement.
Verify that open cuts in the roadway pavement is properly backfilled per plans. If VERMEER trench cutting is used, ensure that backfill with flowable fill is not placed above the top of subgrade to allow subsurface water flow through the pavement structure.
Check that trench backfilling includes the placement of two layers of detectable warning tapes, placed as shown on the plans for underground conduits installation.
Verify that lateral shift in alignment of conduits follow the Flexible Sweep detail in the plans and in accordance with the conduits manufacturer requirements. Must maintain the minimum radius on the inner edge of the bent conduit to avoid introducing excessive pull tension for the fiber optic cabling.
Verify that RMC enter the junction boxes, hand holes, and pull boxes at right angles, extend 1.5” to 3” into the box, and terminated with approved bushing or end bell per specs and plan details.
Check that PVC conduits are terminated flush with the inside face of the junction boxes. Ensure that PVCs are squarely cut, remove any burrs and sharp edges.
Verify that expansion fittings are provided for expansion joints as shown on the plans or as directed by the engineer at bridges and other crossing structures.
Ensure PVC Conduits should be installed with a printed line ““INSTALL THIS SIDE UP – Connecticut D.O.T. Cable – For Assistance Call 860-594-3447”.
Verify that pull wire, rope, or mule tape is securely installed in all conduits, that open conduit ends are capped in the controller base, poles, junction boxes, or pedestals with approved moisture resistant expansion caps or duct sealant.
Verify that all conduits are properly bonded with correct bonding wire per plans and specs.
Ensure complete restoration of the trench excavation areas to the original grade line and conditions per the plan details for roadway trench restoration.
Install 4” X 4” Indentification Posts at intervals identified in the conduit special provision.
Manhole, Handhole and Pull Box Structure:
Ensure all shop drawings for precast units have been reviewed and approved prior to fabrication and installation.
Verify that structure meet the type and size as shown on the plans and / or approved shop drawings, and must be delivered with PC-1 Certification.
Check the excavation for depth and width, and properly compact the 6” Granular Fill bedding. Backfill excavation in properly compacted lifts per standard specs.
Verify that structure is installed with its top finished surface (with frame and cover) level and less than 1” above the surrounding ground.
Check that the structures are not located in the roadway pavement, driveways, parking lot or drainage swale.
Verify that grounding rods are correctly installed in the structure as noted on plans.
Check that the trace or tone wires are continuous from structure to structure.
Verify that the cable rack inserts and assemblies meet plans and specifications.
Verify that all used punch-outs are grouted.
Foundations for Camera-Lowering Device Pole, VMS Support, VMS Cabinet, HAR Pole, Traffic Management System Cabinets and Service Cabinets:
Verify foundation excavation for proper depth and size.
Monitor excavation per OSHA requirements for shoring.
Verify formwork for correct layout, elevation and plumbness.
Check steel reinforcement per approved shop drawing.
Check all anchor bolts and conduits are installed correctly and held securely in place during concrete placement.
Check cast-in-place concrete foundation for slump, air voids, and cast cylinders.
Check for proper backfilling in lifts after concrete have achieved design strength.
Verify the installation of correct grounding rod per plans.
Verify installation of concrete sidewalk at VMS Cabinets and Traffic Management System Cabinets.
Poles for Camera-Lowering Device, HAR Antenna, and Traffic-Flow Monitor Detector:
Verify that the fabricated poles meet the plan size, and no deficiencies found.
Verify the pre-wiring of the poles prior to installation.
Verify the anchor bolts pattern, the orientation of bolts and the installation of the leveling nuts on the foundation per plans. No field adjustment of the bolt holes.
Review Camera-Lowering Device Pole drawings for suggested erection procedure.
Check for required vertical clearance and separation from existing overhead utility.
Verify the torque wrench tightening of the anchor bolts and plumbness of pole.
Verify installation of the closed cell elastomer ring between pole base and foundation.
VMS Supports (Overhead Truss, Cantilever, and Side Mount):
Verify that the fabricated support structure meets approved shop drawings.
Verify pre-wiring of the supports prior to installation of the VMS.
Verify the field location of the supports, plumbness, and correct installation of the horizontal members.
Check the orientation of the horizontal members and the height of the VMS over the roadway for required vertical clearance.
Verify the torque wrench tightening of the nuts at the support anchor bolts.
Ensure all handhole covers are installed correctly after wiring.
Cabling and Splicing (Twisted Pair Cable, Coaxial Cable, Fiber Optic Cable):
Verify the fiber optic cable size, type, fiber counts, date of manufacture, cable length per reel, Optical Time Domain Reflectometer (OTDR) test results per contract special provisions.
Review length of all runs between pulling locations, not to exceed approved cable pulling lengths. Use the sequential cable lengths marked in feet on the cables.
Check with the manufacturer technical representative for installation guidance.
Verify that conduit bushing (duct guards)/end bell with pulling rings are properly installed to prevent cable chafing.
Monitor cable pulling strain gauge per manufacturer requirements.
Ensure proper fiber cable lubricant is used before and during pulling per manufacturer recommendation.
Verify that only fusion splicing is used for the fiber optic cables in a controlled environment.
Verify that the specified cable slack is provided in each junction box at both ends.
Verify that the slacked cables are looped and wire-tied on the cable racks.
Check that cable pulling is done by hand or with approved mechanical cable puller.
Verify that all cabling are properly identified and tagged at the terminal locations.
Maintain record of as-built plans and wiring diagrams.
Ensure that external wiring at the poles / supports are shaped to include a drip loop at each device, and the terminals are well connected to the devices.
Verify the continuity testing of all wires and the OTDR traces for each color coded fiber cable.
Verify that the splice loss for any fusion splice is less than the maximum 0.1 db bidirectional reading per splice.
Verify that trunkline fiber optic cables are placed in the bottom innerduct.
CCTV Cameras, Traffic-Flow Monitor Detectors, and VMS:
Verify that the specified equipment type is installed per plans and specs.
Ensure that the required functional tests are performed in the field successfully.
Check that the equipment is remotely tested successfully from the Highway Operations Center.
Traffic Operation Center Equipment and Others:
List of Operations Equipment:
Network Server / Monitor / Keyboard
Database server / Monitor / Keyboard
Video Server / Monitor / Keyboard
Communications Server / Monitor / Keyboard
Video Switcher Card Cage
Video Switcher CPU Cage
Transceiver F/O Cage (xx cards)
Transceiver F/O
Digi –Board Concentrator
Ethernet Bridge Cage (x cards)
Modem Cage (x cards – data, video, voice)
Modify Existing Operations Center Control System
Equipment Rack
Camera Prototype
Traffic Management System Cabinet
Traffic Management System Mini-Hub Cabinet
CCTV Camera Assembly
VMS
Traffic-Flow Monitor Detector
Ensure that the specified equipment is in accordance with the plans, specifications, approved shop drawings, manufacturers cat cuts, and installed as designated.
Verify that all field equipment cabinet are installed on the foundation with correct conduit / raceway entering the cabinet from the bottom, properly sealed with approved duct sealant, and the cabinets are grounded to the grounding rods.
Verify correct installation of the environmental controls (A/C thermostat, A/C humidstat, Heater thermostat, and Fan thermostat).
Verify the connection of the communication cables to the equipments and patch panels per plans and manufacturer details.
Verify field tests are performed successfully to ensure correct operation of the equipments for video and data transmission.
Ensure contractor provides the required as-built documentations and owner’s manual for maintenance of the system.