SECTION 300500 – TEMPORARY MAINTENACE WORK AREA

- GENERAL	[Sample based on recent projects.]

      - SUMMARY:

        - The Contractor shall provide temporary facilities for the exclusive use of Department personnel.

        - The Contractor shall:

          - Rent (1) Personnel Office Trailer.

          - Purchase (1) Personnel Break Trailer.

          - Rent (1) Personnel Restroom Trailer.

          - Purchase (2) storage containers to supplement (2) existing storage containers.

          - Set-up all temporary facilities on the Project Site.

          - Connect all temporary facilities to all utilities and support services.

          - Make all temporary facilities fully functional and acceptable to the Engineer prior to the start of demolition of the existing building or the existing motor fuel island.

        - The Department will make the following materials available to the Contractor for pickup at the Department’s maintenance facility located at 1640 Saybrook Road, Haddam, CT to establish the temporary facilities:

          - 2,000 gallon Aboveground Storage Tank.

          - Access Stairs.

          - Fuel Dispenser.

          - Fuel Management Unit.

          - Nozzle and Hose.

          - Filter and Adapter.

Contact Mr. Jeffrey Tedesco at (860) 666-8568 a minimum of 72 hours in advance to make arrangements to pick up materials.

        - The Owner will relocate personnel and materials such as office furniture, tools, and equipment from the existing facility into the temporary trailers.  Upon completion of the Project, the Owner will return said items back to the renovated facility.

        - Temporary facilities shall remain on the Project Site for the duration of the Project, including Contract time extensions if any occur, and if required for a maximum of 30 days thereafter.

        - Temporary facilities shall be removed from the Project Site as described herein, unless otherwise noted.

      - SUBMITTALS:

        - Submit the following in accordance with Form 817 Article 1.20-1.05.02 and NOTICE TO CONTRACTOR – SUBMITTALS for the fuel dispensing equipment.

        - Product Data: For each type of product indicated.

        - Shop Drawings: For each type of product indicated.

        - The Engineer will approve the remaining materials to be installed by the Contractor, unless otherwise noted.

      - COORDINATION:

        - Electrical Service:  Refer to CSI Division 26 Section 262713, “Electricity Metering.”  Temporary electric service shall be installed as shown on the plans. The work includes furnishing temporary tripods, electric meters, all the trenching and backfilling, conduits, conductors, electrical panels, weatherheads, etc. as required by Eversource and necessary to feed all the associated temporary electrical loads.

        - Communications Service:  Refer to CSI Division 27 Section 270000, “Premises Telephone Wiring.”  Temporary communications service shall be installed as shown on the drawings. The work includes furnishing temporary d-marc boxes, all the trenching and backfilling, conduits, conductors, weatherheads, etc. as required by Frontier and necessary to feed all the associated temporary telephone/facsimile/internet lines.

- PRODUCTS

      - PERSONNEL OFFICE TRAILERS:

        - The personnel offices shall be pre-manufactured office trailers, altered as necessary to provide the required specified items.

          - Minimum Trailer Size: 10-feet by 40-feet.

          - Minimum Ceiling Height: 7-feet.

        - Windows shall open and close conveniently, shall be sufficient in number and size to provide adequate light and ventilation, and shall be fitted with locking devices, blinds, and screens.

        - The office trailers shall have two operable entrances.  The entrance doors shall be fitted with locks.  Lockset shall accept 7 pin small format interchangeable core.  Cores will be provided by the Owner.

        - Stairs, handrails, and landings shall be provided to meet all applicable building codes for all trailers.

        - Interior Lighting: Electric lighting that provides a minimum illumination level of 40 foot-candles at desk level height. The Contractor shall also provide emergency battery back-up lighting throughout the trailer and on the exterior focused on illuminating the exits.

        - Exterior Lighting: Provide exterior lighting on the entrances/exits of each trailer. Fixture shall be LED wallpack, 4000K, 2500lumens minimum, with photo control. Lithonia Model No. TWR1 or an approved equal.

        - Exit Signs and Lighting: as required by code.

        - The Contractor shall provide containerized tap-dispenser bottled-water type drinking water units in 5-gallon capacities, including paper supply for temporary office in ample and continuous supply.  Provide (1) electric sanitary water cooler per trailer to maintain dispensed water temperature at 45 to 55oF.

        - The trailers shall be equipped with sufficient heating and air conditioning equipment to maintain a temperature range of 68o-80o Fahrenheit within the trailers.

        - Each personnel trailer shall be pre-wired to a 100-125A electrical distribution panel to serve the electrical requirements of the trailer such as lighting, general 15A duplex receptacles, (1) exterior GFCI receptacle. The Contractor shall install and maintain electrical service to each personnel trailer. The Contractor shall conform to all applicable requirements of the NEC. Trailers shall be compatible with the available voltage and phasing as indicated on plans.

        - Each personnel trailer shall be pre-wired to an electrical distribution panel to serve the electrical requirements of the office such as lighting, general 15A duplex receptacles, and computer outlets, and shall meet the following specifications: all panels shall include a main circuit breaker and branch circuit breakers of the size and quantity required.  The Contractor shall conform to all applicable requirements of the NEC.

        - The Contractor shall provide and install (3) hard-wired with battery back-up smoke detectors in each trailer.

        - The Contractor shall provide and install all necessary telephone and data cable and connections to service and complete the Personnel Office Trailers and the fuel dispensing island.

        - The Contractor shall complete temporary phone system wiring from the Dmarc boxes into the Personnel Office Trailers.  The Contractor shall complete punch-down connections.  The Contractor shall also provide all temporary conduit raceways between trailers.  The number of phone lines, fax lines, modem lines, and internet lines shall be as required to maintain the level of service in the existing facility.

        - The Contractor shall provide and install communications cabling as required by the plans.  The Engineer will contact the ConnDOT Office of Information Systems to coordinate related work.

        - The Owner will provide all telephones. Refer to CSI Division 27 Contract provisions for further requirements regarding telephone and data systems. The Owner will pay all telephone and data use charges to the Personnel Office Trailers.

      - PERSONNEL BREAK TRAILERS:

        - The personnel break trailers shall be CORE 10 steel shipping containers, painted with manufacturer’s standard exterior grade paint, altered as necessary to provide the required specified items.

          - Minimum Trailer Size: [8 feet by 20-feet][8 feet by 40-feet (for 8 employees)].

          - Minimum Ceiling Height: 7-feet.

          - Each trailer shall be provided with permanent concealed lifting points for placement and for future relocation.  Each trailer shall be suitably braced, wrapped, and secured for transportation.

        - Interior Floor Construction: 2-inch by 4-inch framing 16-inches on center, R-11 commercial grade spray-applied insulation, with ¾-inch plywood and epoxy or vinyl covering.  Include 4 mil poly between container and framing.

        - Interior Wall Construction: 2-inch by 3-inch framing 16-inches on center, R-11 commercial grade spray-applied insulation, with plywood and white vinyl laminate or wood paneling.  Base trim shall be 4-inch wide vinyl cove molding. Include 4 mil poly between container and framing.

        - Interior Ceiling Construction: 2-inch by 4-inch framing 16-inches on center, R-11 commercial grade spray-applied insulation, with ½-inch paneling.  Include 4 mil poly between container and framing.

        - Windows, Horizontal Sliding: Shall open and close conveniently, shall be sufficient in number and size to provide adequate light and ventilation, and shall be fitted with locking devices, blinds, double-pane glass, and screens.  Provide 2x2x12 ga. steel tube framing for security bars.

        - Doors: (2), 36-inch by 80-inch steel entry doors with interior push bar with 10”x10” window, exterior lever handle, interior kick plate, heavy duty door closer, and locks.  Lockset shall accept 7 pin small format interchangeable core.  Cores will be provided by the Owner.

        - The trailers shall be equipped with sufficient heating and air conditioning equipment to maintain a temperature range of 68o-80o Fahrenheit within the trailers. Provide 2x2x12 ga. steel tube framing for security bars.

        - The Contractor shall install and maintain electrical service to each personnel break trailer.  The Contractor shall conform to all applicable requirements of the NEC. Trailers shall be compatible with the available voltage and phasing as indicated on plans. The panel box shall be installed at the front of the trailer so conduit bodies will be on the front of the trailer to avoid damage during loading/unloading of the trailer.

        - Each personnel trailer shall be pre-wired to a 100-125A electrical distribution panel to serve the electrical requirements of the trailer such as lighting, general 15A duplex receptacles, (1) exterior GFCI receptacle, and shall be compatible with the available voltage and phasing as indicated on plans.  All panels shall include a main circuit breaker and branch circuit breakers of the size and quantity required.

        - Interior Lighting: Electric lighting that provides a minimum illumination level of 40 foot-candles at desk level height. The Contractor shall also provide emergency lighting throughout the trailer.

        - Exterior Lighting: Provide exterior lighting on the entrances/exits of each trailer. Fixture shall be LED wallpack, 4000K, 2500lumens minimum, with photo control. Lithonia Model No. TWR1 or an approved equal.

        - Exit Signs and Lighting: as required by code.

        - The Contractor shall provide containerized tap-dispenser bottled-water type drinking water units in 5-gallon capacities, including paper supply for temporary office in ample and continuous supply.  Provide (1) electric sanitary water cooler per trailer to maintain dispensed water temperature at 45 to 55oF.

        - The Contractor shall provide and install (3) hard-wired with battery back-up smoke detectors and (1) plug-in CO detector in each trailer.

        - Contractor shall provide and install all necessary telephone and data cable and connections to service and complete the Personnel Break Trailers.

        - The Contractor shall provide and install communications cabling as required by the plans.  The Engineer will contact the ConnDOT Office of Information Systems to coordinate related work.

        - The Owner will provide all telephones. Refer to CSI Division 27 Contract provisions for further requirements regarding telephone and data systems. The Owner will pay all telephone and data use charges to the Personnel Office Trailers.

      - PERSONNEL RESTROOM TRAILER:

        - Basis-of-Design: Restroom trailer designed for high traffic and high abuse settings, R-14 Deluxe Trailer available from United Site Services, or an approved equal.

          - Approximate Trailer Size: 9-feet by 26-feet.

          - Minimum Ceiling Height: 7-feet.

        - Trailer Layout:

          - Men’s: (1) toilet, (1) sink, (3) urinals.

          - Women’s: (3) toilets, (1) sink.

        - The trailer shall be equipped with sufficient heating, air conditioning and ventilation equipment to maintain a temperature range of 68o-80o Fahrenheit within the trailers.

        - The trailer shall be equipped with a water heater to provide hot water at the sinks.

        - The entrance doors shall be fitted with locks.  Lockset shall accept 7 pin small format interchangeable core.  Cores will be provided by the Owner.

        - Stairs, handrails, and landings shall be provided to meet all applicable building codes for all trailers.

        - Accessories: Provide trash receptacles, mirrors, soap dispensers, paper towel dispensers, and GFCI receptacles.

        - Interior Lighting: The Contractor shall equip the interior with sufficient electric lighting for the trailer’s use as a restroom.  The Contractor shall also provide emergency lighting throughout the trailer.

        - Exterior Lighting: Provide exterior lighting on the entrances/exits of each trailer. Fixture shall be LED wallpack, 4000K, 2500lumens minimum, with photo control. Lithonia Model No. TWR1 or an approved equal.

        - Exit Signs and Lighting: as required by code.

        - The Contractor shall install a trailer skirt between the bottom of the trailer and grade.  The skirts shall be made of Texture 111, or equal.

        - The Contractor shall install and maintain water service from the existing well to the Personnel Restroom Trailer as shown on the plans.  Heat tracing shall be provided and maintained.

        - The Contractor shall install a septic tank and maintain a sanitary waste pipe from the Personnel Restroom Trailer to the septic tank as shown on the plans.  Heat tracing shall be provided and maintained.

        - The Contractor shall install and maintain electrical service to the restroom trailer.  The Contractor shall conform to all applicable requirements of the NEC. Trailers shall be compatible with the available voltage and phasing as indicated on plans.

      - STORAGE CONTAINERS:

        - The storage containers shall be weatherproof and of all steel construction with integral steel skids for ground level placement and accessibility.  Tractor-trailer storage is not acceptable.

          - Minimum Trailer Size: 8-feet by 40-feet.

          - Minimum Ceiling Height: 7-feet.

        - Storage containers shall include heavy-duty double steel doors with locking bars located at one end of unit.  Doors shall include provisions for Owner supplied padlocks.

        - A minimum of 2 overhead electric lights shall be provided in one storage container. Lighting shall be a 4 foot linear type fixture, rated for wet location, suitable for interior and exterior installation. Cree Model No. WS4 47L 40K 10V FD SSL, or an approved equal. The fixture, workbox, conduit, and associated electrical equipment shall be fastened with corrosion resistant hardware as specified under CSI Division 26 Section 260529, "Hangers and Supports for Electrical Systems."

        - One storage container shall be equipped with electrical distribution to the following specifications: 120/208 volt, single phase, 3 wire sub-feed from the power source shown on the plans.  The Contractor shall conform to all applicable requirements of the NEC.

      - FUEL DISPENSING ISLAND:

        - Compacted Granular Fill:  Refer to Form 817, Section 2.14 “Compacted Granular Fill” for material and construction methods required.

        - Concrete Pads: Comply with the requirements in CSI Division 03 Section 033000, “Cast-in-Place Concrete.”

        - Precast Concrete Barriers: Refer to Form 817, Section 8.21 “Precast Concrete Barrier Curb” for material and construction methods required.

        - Temporary Steel Plate:  1” thick steel plate, conforming to ASTM A36, with minimum dimensions as shown on the plans.

        - The fuel dispensing equipment (tank, tank accessories, fuel dispenser, FMU, emergency controls and miscellaneous components) shall meet all of the applicable regulatory requirements set forth by ASTM, NFPA, STI, and UL.

        - The Contractor shall provide mounting hardware and miscellaneous parts to complete installation.

        - Floodlight and Support:  The floodlights shall be rugged, weather resistant die-cast aluminum with gasket, and shall be equipped with a photocell for Dusk-to-Dawn operation. Lithonia Model No. OFTH300PR with two 90 Watt lamps, 120 Volts, and photocell, or an approved equal. The mast support for the lights shall be composed of steel c-channel as specified under CSI Division 26 Section 260529, "Hangers and Supports for Electrical Systems."

        - The Contractor shall use threaded RGSC for all power and communication feeds when conduits enter into a Class I, Division 1/Division 2 hazardous location and for all surface mounted conduit around the dispenser as shown on Drawing No. ET-001.

        - The Contractor shall use a minimum #12 stranded copper conductors rated for 600 volts with THWN or THNN insulation within the Class I, Division 1 hazardous location unless otherwise noted.  Grounding wire shall be green-type.

        - Junction Boxes shall be threaded, explosion-proof, Model No. GRSS-2 as manufactured by Killark, or an approved equal.

        - Explosion-proof fittings shall be threaded, recessed-type, close-up plugs, Model No. EYSF75 as manufactured by Appleton, or an approved equal.  Screwdriver slotted close-up plugs shall not be accepted. When necessary to employ flexible connections, as at motor terminals, flexible fittings listed for Class I locations shall be used.

        - Conduit Seals shall be approved for Class I, Division I locations as described in section 501-15(a)-(f) of the NEC.  Sealing compound shall be approved and shall provide a seal against passage of gas or vapors through the seal fitting, shall not be affected by the surrounding atmosphere or liquids, shall not have melting point of less than 200 degrees F.  In a completed seal, the minimum thickness of the sealing compound shall no be less than the trade size of the sealing fitting and, in no case, less than 5/8 inch.

        - Each circuit leading to or through dispensing equipment, including equipment for remote pumping systems, shall be provided with a clearly identified and readily accessible switch or other acceptable means, located remote from the dispensing device, to disconnect simultaneously from the source of supply, all conductors of the circuit, including the grounded (neutral) conductor. Emergency controls shall be more than 20 feet but less than 100 feet from the dispenser.

        - Emergency Shut-off (Quick Stop Button): The quick stop button functions to remove power by depressing the red mushroom-shaped button.  Power restored by manually resetting the shunt trip device and turning the button clockwise a partial turn until it pops back out to the reset position.

        - The dispenser shall be controlled by the dispenser’s “on/off” handle at the point of fuel distribution and remotely by the circuit breaker.

        - Fixed wiring: Threaded RGSC with termination fittings and wiring methods approved for Class I location shall be employed. All boxes, fittings and joints shall be threaded for connection to conduit and shall be explosion-proof. Threaded joints shall be made up with at least 5 threads fully engaged.

        - Grounding: All metal raceways and all non-current carrying metal parts of fixed or portable electrical equipment, regardless of voltage, shall be grounded as provided in NEC Article 250 and per Article 514-16. The locknut–bushing and double-locknut types of contacts shall not be depended on for bonding purposes, but bonding jumpers with proper fittings shall be used. Such means of bonding shall apply to all intervening raceways, fittings, boxes, enclosures, etc., between Class I location and the point of grounding for service equipment. Bonding shall be jumpers with proper fittings for bonding purposes.

        - An approved seal shall be provided in each conduit run entering or leaving a dispenser or any cavities or enclosures in direct communication therewith. The sealing fitting shall be the first fitting after the conduit emerges from the earth or the concrete.

        - Splices and taps shall not be made in fittings intended only for sealing with compound, nor shall other fittings in which splices or taps are made be filled with compound.

        - The cross-sectional area of the conductors permitted in a seal shall not exceed 25% of the cross-sectional area of a RGSC of the same trade.

- EXECUTION

      - INSTALLATION, GENERAL:

        - The Contractor shall locate temporary facilities where shown on the plans and as directed by the Engineer.  The temporary facilities shall be installed in accordance with Form 817 Article 1.08.02, as supplemented herein.

        - The Contractor shall level and secure all Personnel Office Trailers, Personnel Break Trailers, and the Personnel Restroom Trailers as directed by the Engineer and in accordance with manufacturer’s recommendations.

        - The Contractor shall provide applicable utility extensions to all trailers and storage containers. Water service and sanitary sewer extensions for trailers shall be protected from freezing by installation at 48 inches below grade, and with the proper use of insulation and electric heat tape for locations above the frost line.

        - Block Heater Area Floodlight and Support: The Contractor shall firmly attach the c-channel mast to the wooden block heater post. The Contractor shall install a surface mounted metallic box to attach the floodlights to the mast. The Contractor shall install a single gang box rated for exterior use and single pole switch with exterior switch cover, wired to control the floodlights. Route surface mounted RGSC conduit along the c-channel to feed the floodlights.

      - INSTALLATION, FUEL DISPENSING ISLAND:

        - The Contractor shall install each component of the fuel dispensing island as shown on the plans, in accordance with manufacturer’s installation instructions, and in accordance with NFPA 30 and 30A.  Additional installation requirements are described herein, where applicable.  The Contractor shall provide a fully operational system when complete.

        - The Contractor shall modify the AST and dispenser as necessary to be used to store and dispense diesel fuel. The Contractor shall verify fuel dispenser is secured to tank and all necessary piping connections are completed.

        - The Contractor shall verify the existing fill assembly complies with the requirements of NFPA 30A and incorporates the following features:

          - A lockable tight fill cap, adapter, fill pipe, and drop tube.

          - The bottom of the fill drop tube shall be cut at a 45-degree angle with the open end facing the long dimension of the tank.

          - The drop tube shall terminate 6-inches from the bottom of the tank.

        - The Contractor shall verify the existing overfill prevention equipment complies with the requirements of NFPA 30A and incorporates the following features:

          - An audible alarm which will sound when the product level in the tank has reached 85% of tank capacity, or a liquid level gauge marked at 85% of tank capacity.

          - A positive shut-off fill limiter which will stop the flow of liquid into the tank when product level reaches 90% of tank capacity.

          - The fill-limiting device shall be rated to accept the fill flow rate and pressure.

        - The Contractor shall verify the existing product piping at the tank includes and anti-siphon device that will prevent the flow of liquid from the tank unless the suction pump is operating, in accordance with NFPA 30A.

        - The Contractor shall verify that a pressure relief valve is included in each segment of blocked piping that will relieve excessive pressure resulting from thermal expansion and return any excess product to the tank.

        - The tank and associated equipment shall be installed in accordance with the STI installation instructions for Fireguard aboveground tanks (Publication No. R942-94, Installation and Testing Instructions for Thermally Insulated Lightweight Double Wall Fireguard Aboveground Storage Tanks).

        - The Contractor shall (1) use tank handling equipment of adequate size to lift and set the tank without dragging or dropping it; (2) advise the Engineer of any shipping or handling damage encountered; and (3) not make any modifications to any tank without the prior written approval of the manufacturer and the Engineer. Such modifications include any welding on tank shells, adding penetrations in the tank structure, or repairing damage that might affect the integrity of the inner or outer tank.

        - The Contractor shall locate the temporary steel plate where shown on the plans and as directed by the Engineer.

        - The Contractor shall locate precast concrete barriers where shown on the plans and as directed by the Engineer.

        - The Contractor shall protect existing exposed piping and equipment from corrosion by painting or wrapping it with a coating that is compatible with diesel fuel and the conditions of the exposure.

        - The Contractor shall locate the concrete pad for the temporary FMU where shown on the plans and as directed by the Engineer.

        - Install temporary FMU and retrofit to work with dispenser.

        - Provide a fully operational temporary automated fuel management system. The temporary FMU shall interface with the existing head-end located at 2800 Berlin Turnpike, Newington, CT. Coordinate dial-up programming with the Department Fuel Control. The following information shall be recorded by the system for each fueling transaction: user identification number, vehicle odometer/hourmeter, vehicle number, quantity of fuel dispensed, fuel site, date and time, hose number and product number, and key type.

        - FMU Power Requirements: 120 volts, 60 Hz, from a separate dedicated circuit.

        - Floodlight and Support: The Contractor shall firmly attach the c-channel mast to the precast concrete barrier. The Contractor shall install a surface mounted metallic box to attach the floodlights to the mast. Route surface mounted RGSC conduit along the c-channel to feed the floodlights.

        - The Contractor shall install all conduit, boxes, and wiring in accordance to NFPA 70 and shall run green bond wire in all conduits.

        - The Contractor shall install RGSC from the source of power to the fuel dispensing system, and complete conduit, terminations with explosion-proof fittings.  All E.Y. fittings for conduit runs to the fuel island shall be properly sealed.  The Contractor shall leave close-up plugs hand tight after sealing to provide for the Engineer’s inspection of these fittings.

        - The Contractor shall extend fuel dispensing island power and communication circuits from the power panels and communication cabinets in the temporary service area to the temporary fuel island location. The Contractor shall complete all necessary terminations in accordance with NEC Article 514 and sections described above.

        - The Contractor shall perform air pressure testing of the inner tank and secondary containment tank on-site in the presence of the Engineer before placing the tank in service.  Refer to STI Publication No. R942-94 for complete procedural details.

        - The Contractor shall test piping on-site in the presence of the Engineer before placing the piping in service. The Contractor shall perform minimum hydrostatic or pneumatic test-pressures measured at highest point in system, minimum 1.5 times the designed working pressure but not less than 5 psig for minimum 2 hours, isolate storage tanks if test pressure in piping will cause pressure in storage tanks to exceed 10 psig and shall soap pipe fittings. Piping will be considered defective if it does not pass tests.  Defective piping shall be repaired or replaced, and then retested.

        - The Contractor shall test each component of the system for calibration, tightness and proper operation in accordance with the instructions of the component manufacturer.

        - Testing shall be documented by the Contractor and witnessed by the Engineer.  Record the date and time of the test, the name of the tester and their affiliation with the Project, and the names of each individual witnessing the test.  The Contractor shall record the test method, duration and results, and provide a record of the testing to the Engineer at the time of system start-up.

        - The Owner will supply diesel fuel to fill the temporary AST upon its acceptance by the Engineer.

      - MAINTENANCE AND REPAIRS:

        - The Contractor shall be responsible for maintenance and repairs to all Personnel Office Trailers, Personnel Break Trailers, Personnel Restroom Trailers, and Storage Containers provided or installed under the above requirements at all times during occupancy by the Department.  The Department will be responsible for maintenance and repairs to the fuel dispensing island.

        - Ownership and liability of the Personnel Break Trailer, Storage Containers and the fuel dispensing island will remain with the Engineer.

      - PROJECT CLOSEOUT:

        - When the Engineer determines that the temporary facilities are no longer needed, the Department will vacate the facilities and empty the temporary AST.

          - Storage Containers will remain on the Project Site as Owner property.

        - The Contractor shall prepare the following Owner equipment for salvage and removal from the Project Site, including but not limited to the removal of connected utilities:

          - Equipment identified in Part 1.1C.

          - Personnel Break Trailer.

          - Septic Tank.

          - Block Heater Area Floodlights and Supports.

          - Personnel and Restroom Trailer Wallpack Lighting.

          - Electrical Meter Socket.

          - Power and Communications Panels and related components on plywood backboards.

          - Fuel Island components and plywood backboards.

          - Temporary Power Wood Pole.

        - The Contractor shall move the Owner property identified in Part 3.4B to the Department’s Maintenance Facility located at 1640 Saybrook Road, Haddam, CT, 06438 within 14 calendar days of their abandonment.

        - The Contractor shall:

          - Demolish all work not identified to be salvaged.

          - Relocate the precast concrete barriers on the Project Site as directed by the Engineer

          - Complete Project Site work.

END OF SECTION 300500