DESIGN MANUAL FOR

MAJOR CAPITAL PROGRAM FACILITIES

AND SALT SHEDS

VERSION 4.6

November 29, 2019

PREFACE

The intent of this Manual is to set forth in a single document particular user requirements for facilities maintained by the Department of Transportation.  This Department wishes to standardize important building features that contribute to an effective work environment.  It should be noted that for the most part there is no building maintenance staff on-site.  In addition, there are certain statewide systems using recognized standards that shall be incorporated in the facilities. Lastly this Department has strong historical information with regard to specific construction types, equipment and controls that maximize the life cycle of the facility.

This Manual will provide guidance for Facilities Design staff and consultants in understanding the operational requirements.  It may be necessary to modify some of the design parameters based on specific project scope requirements.

This Manual is not a static, unchanging directive. It is expected that as conditions and technology change, it will be updated to reflect those conditions.

To minimize the likelihood of errors or conflicting information, the design should try to eliminate the need to edit the specs to the greatest extent possible on each project.  Also, information should not be shown in both the plans and the specifications, even if it says the same thing.  To eliminate the need to modify the specifications on each project, or to deal with forgetting to modify the specification, in general, anything editable should be on the plans.  Examples include, but are not limited to, the following: door hardware schedules, sign schedules, alarm light locations, boilers, etc.

Similarly, code requirements such as wind speeds, snow loads, and seismic requirements, appear in multiple specifications as well as the Structural note plan.  This information should be included only on the Structural note plan.  The specifications can be modified to reference this Structural plan.  Structural designers should also give consideration to developing a “worst case” set of code requirements for the state rather than having specific versions for each municipality.

Many of the topics discussed in this Manual are depicted in recent design projects and design manuals.  Special provisions are primarily based on office standards and CSI-formatted special provisions are based on DELTEK + AVITRU (formerly ARCOM) template specifications modified for office standards.  Plans and specifications are available upon request.

Refer to the “Facilities Design Manual of Responsibilities During Design and Construction” for additional guidance.

NOTE TO USERS:

This Manual has not been reviewed against the 2018 Connecticut Building Code, the 2018 Connecticut Fire Safety Code, and the 2018 Connecticut Fire Prevention Code.  Code requirements of these documents shall govern.  The User is asked to advise the author of this Manual of any perceived conflicts.

TABLE OF CONTENTS

GENERAL DESIGN PARAMETERS								4

CIVIL/SITE											6

DEMOLITION											9

ARCHITECTURAL AND STRUCTURAL PLAN DEVELOPMENT				10

CSI DIVISION 3 – CONCRETE							15

CSI DIVISION 4 – MASONRY							15

CSI DIVISION 5 – METALS 							16

CSI DIVISION 6 – WOOD, PLASTICS, AND COMPOSITES				17

CSI DIVISION 7 – THERMAL AND MOISTURE PROTECTION				18

CSI DIVISION 8 – OPENINGS							19

CSI DIVISION 9 – FINISHES 							21

CSI DIVISION 10 – SPECIALTIES 							22

CSI DIVISION 11 – EQUIPMENT 							24

CSI DIVISION 12 – FURNISHINGS 							24

CSI DIVISION 13 – SPECIAL CONSTRUCTION 						25

CSI DIVISION 14 – CONVEYING EQUIPMENT							27

CSI DIVISION 21 – FIRE SUPPRESSION							27

CSI DIVISION 22 – PLUMBING							28

CSI DIVISION 23 – HEATING, VENTILATING AND AIR CONDITIONING			31

CSI DIVISION 26 – ELECTRICAL 							34

CSI DIVISION 27 – COMMUNICATIONS 							43

CSI DIVISION 28 – ELECTRONIC SAFETY AND SECURITY				46

SALT SHEDS AND PERSONAL SHELTERS						47

SALT SHED REHABILITATION PROJECTS TYPICAL SCOPE OF WORK		48

APPENDIX											49

GENERAL DESIGN PARAMETERS

Codes and Standards:

The design will comply with the following:

State of Connecticut Building Code

https://portal.ct.gov/DAS/Office-of-State-Building-Inspector/Connecticut-State-Building-Code/Regulations

State of Connecticut Fire Safety Code

https://portal.ct.gov/DAS/Office-of-State-Building-Inspector/Building-and-Fire-Code-Adoption-Process

State of Connecticut Fire Prevention Code

https://portal.ct.gov/DAS/Office-of-State-Building-Inspector/Building-and-Fire-Code-Adoption-Process

2010 Department of Justice “ADA Standards for Accessible Design,”

http://www.ada.gov/regs2010/factsheets/2010_Standards_factsheet.html

FM Global Data Sheets

Ground Snow Load: On new construction, exceed the Building Code requirement by 10 psf.

Due to the emergency response nature of a Department maintenance facility, the seismic design will be considered Seismic Use Group III.

Unless otherwise directed by the authority having jurisdiction, projects will be designed to the current code.  If something changes when the new code is in effect a code modification can be issued.  Do not design to the “most restrictive scenario” guessing when the new codes will be issued.

The State of Connecticut “Capital Projects High Performance Building Guidelines” do not apply to maintenance facilities, salt sheds, and parking garages.  They will however apply to office buildings.   Refer to: http://www.ct.gov/dpw/lib/dpw/0450_Capital_Projects_High_Performance_Buildings_Guidelines.pdf

Background Information:

Review ProjectWise and the files in the Office of Property and Facilities Services for the original building plans, any subsequent project plans, and asbestos and lead reports prepared by EnviroMed Services, Inc. in 2001.

Primarily for renovation projects, the decision to relocate or reuse existing systems will be made on a case-by-case basis based on age and obsolescence.  A list of materials to be salvaged will need to be requested from the owner/occupant.

The design will include “lessons learned” from past projects.

Design Support Unit Coordination:

A subsurface geotechnical investigation will be performed.  Structural boring locations will be identified for footings and foundations and site boring locations will be identified for site elements including but not limited to tanks.

Environmental Compliance investigations for soil and groundwater, asbestos and lead, and other hazards will be performed.

Pavement Management determinations and Traffic coordination will be performed on a project specific basis.

Construction Considerations:

Temporary Facilities for Department Personnel to use during construction will be provided for employees as needed and as will be permitted with the tight site constraints.  The required temporary facilities will be verified early in the project.  Typical projects require:

- (1) Medium Office Trailer per operational group (Maintenance, Bridge, Electrical, Repair and Stores, Signs and Markings, etc.).

- Rest Break Trailer per operational group. Refer to Appendix 4 for the floor plans of the rest break containers that we have for maintenance. Also here is the contract link for them http://www.biznet.ct.gov/SCP_Search/ContractDetail.aspx?ID=16886

- Bathroom Trailers (Repair and Stores share one and the remaining operational groups share a second one).

- Storage Containers, 8-ft wide by 40-ft long, $3,900 each in 2014.

- Hazmat Storage Container, 7-ft wide by 9-ft long, 4 hour rated; C&E Storage Model CE1200-FR4 has been used, $14,000 each in 2017.

- Temporary Motor Fuel Island: Provide temporary aboveground storage tanks for diesel fuel and gasoline (if required by Fuel Control) if the existing motor fuel island cannot remain operational.

Staff Maintenance has requested that provisions (manual transfer switch, generator subpanel, etc.) shall be provided for all projects where DOT operations relocate to temporary trailers.  Desired loads include the office trailer, break trailer, bathroom trailer HVAC and lighting along with the fuel station and sanitary pump stations if possible.  Load shedding is acceptable (for example the HVAC can be shut off to run the fuel island).  Omitted loads include the chloride system and site lighting.  Site lighting requirements could be met on an as needed basis by using Bridge light towers.  Staff Maintenance will investigate the acquisition of a portable generator on a trailer for each District that could be moved to a site on an as needed basis.

In the past, DOT has been able to use National Guard assets under the big storm scenario.

Plow Truck Salt Capacities:

When Maintenance was using the 7:2 sand/salt mixture a 9 ton plow had 8 miles worth of material on board.  Now with straight salt this has increased to 24 miles.  A 10 wheeler has 50 miles of material on board.  This may permit some facility consolidations or relocations.

CIVIL/SITE

SITE LAYOUT

Operational Clearances:

Clear space in front of Bay Areas = 60-feet

Operational space in front of a Salt Shed = 90-feet

FM Global (ideal) separation distance between the fuel island and building = 75-feet

Perimeter Access:

A minimum 15-foot wide paved area is required around the entire perimeter of the building for plowing access unless the site constraints do not permit.  This paved area is required for building egress and maintenance access purposes.  Ideally, a Payloader should be able to get around the building.

Sidewalks:

If required, sidewalks will be paved and will be 10-feet wide to facilitate snow removal.

Parking Spaces:

The number of parking spaces will be determined by the building occupant load, plus visitor spaces, plus handicap spaces.

Overhead Door Approach Slabs:

Consider the use of concrete pavement for approaches into the bays since paving between the bollards is very difficult and results in segregation.  At Repair facilities, 40-foot long slabs shall be installed in front of select doors to permit repair activities such as lifting vehicles off the ground.

Flag Pole:

A lighted flag pole will be located at all occupied building sites.

Dumpster Pad:

Dumpster pads will be based on 40 CY (20-foot by 8-foot) dumpsters.  Maintenance facilities will include a 22’ by 28’ dumpster pad sized for (2) dumpsters.  Specialty facilities including but not limited to Repair and Bridge will include a 22’ by 40’ dumpster pad sized for (3) dumpsters.  Use epoxy coated rebar.

Loading Dock:

A loading dock will be constructed at salt sheds if requested by Staff Maintenance.  The Payloader operator's eyes want to be level with the top of the Payloader.  This equates to a 3-foot tall ramp with a 4-foot tall wall at the edge of the ramp.  Use epoxy coated rebar.  Include a railing system.

Storage Bins:

Areas for concrete block or precast concrete barrier curb storage bins will be provided at sites to maintain an organized, clean site.  Location and configuration will be as requested by the facility occupants.  Typically, the blocks are not provided by the project.  Include covered storage for cold patch and other materials such as galvanized metals as required by Maintenance.

UTILITIES

Water:

A public water supply system is preferred for all locations when within reasonable proximity.  The Owner will be the ultimate arbiter of “reasonable.”

If public water is unavailable, a well water system will be required.  Investigate the condition of the existing well (coliform issues, low pressure and volume) and replace the well or the well pump if necessary.  The basic system design has the well pump filling an underground 5,000 gallon water storage tank.  Operationally, the well control system will be based on float-style switches as opposed to electrodes.  Pressurized tanks inside the building will be supplied by a submersible pump inside the water storage tank.

Sewer:

Bay Area drain outflow will drain to a wastewater holding tank, or if at all possible, to an oil/water separator and municipal sewers.  If a municipal system is reasonably close, it is certainly worth looking at the cost of municipal hookup.  It becomes very expensive to pump and dispose of waste water.  The Owner will be the ultimate arbiter of “reasonable.”  If a public sewer is not available, a septic tank and leeching field will be installed.

Manholes will be used at junctions of trench drain pipes in lieu of fittings to facilitate cleanout and maintenance.  These manholes will not have any sumps.  A manhole with a 4-foot deep sump and a drop inlet will be installed immediately prior to each oil-water separator to function as a grit separator.

Septic system and trench drain system manhole covers will be gasketed and watertight.

Gas:

Natural gas is preferred for all locations when within reasonable proximity.  The Owner will be the ultimate arbiter of “reasonable.”

OTHER SITE ELEMENTS

Chain Link Fencing and Gates:

All fencing will have top rail and it is requested that the entire site be fenced.  The fencing of a site may have severe public opposition.  A final decision on fencing will take into consideration the Public Involvement Process.  The need for a fenced storage compound will be discussed with the facility occupants.  Coordinate with the facility occupants to include snow gates to permit snow removal operations.  If the site is not fully fenced, all aboveground fuel (motor fuel and fuel oil) storage tanks shall be enclosed by a fence with PVC slats and shall include a 6’ wide gate.  All gates shall include 2 ring bolts instead of the standard locking hardware.  These bolts shall be set to accept a state-furnished padlock.  Continue to use the drop rods on double-leaf gates.

Bollards:

Bollards will be provided to offer protection around all aboveground fuel storage tanks, generators, transformers, garage doors, exposed corners of facilities, and elsewhere as required on a specific project.  Bollards will be 8-inch diameter and sleeved with a yellow polyethylene cover.  Unless otherwise necessary, the centerline of the bollards at the garage doors shall be 5’-4” off the outside face of the building.  Steel bollards are required in locations where electrical conduit is exposed to vehicular traffic.

Storm Drainage:

Catch basins will have 2-foot deep sumps unless the project is located in an environmentally sensitive area where 4-foot deep sumps may be requested.

Detention basin with fore-bay is the desired primary treatment for site runoff.  On sites where primary treatment is not possible, secondary treatment in the form of a hydrodynamic separator will be used.

The use of swales and natural runoff areas (no curbing) are encouraged.  A rip rap splash pad will be used at all culvert ends/ outflow points.

Landscaping:

Turf establishment will be used in non-pavement areas.  To facilitate maintenance, slopes should not exceed 3 to 1.  To minimize maintenance needs, stone will be used in non-pavement areas when possible around storage tanks, generators, sheds and elsewhere as required by the project.

More extensive landscaping may be required on sites in politically and/or publically sensitive areas.

Paving Fabric:

A layer of paving fabric will be placed between bituminous lifts within the interior of the salt sheds and within the salt shed operational areas.

Sedimentation and Erosion Controls/Anti-tracking Pads:

Install and maintain sedimentation controls at the toe of slopes and around catch basins in areas of erodible soil during construction.  Sedimentation controls shall be installed at all site outflow points. Anti-tracking pad will be installed on every site during construction.  A concrete washout shall be included in projects that involve concrete work.

Chloride Tank Storage and Distribution System:

All operational salt shed sites will include a chloride tank storage and distribution system. The storage tank will be double-wall, polyethylene, sized from 5000 to 6500 gallons; manufactured by Snyder Industries at (402) 465-1230. The fluid level in the tank will be monitored by an ultrasonic level gauge with tank-mounted digital readout.  Use epoxy coated rebar.

Each tank will have a fluid distribution system controlled by a momentary contact push button, and will consist of a self-priming centrifugal pump mounted in a secondary containment enclosure, flexible hose, and polypropylene valves and fittings compatible with DOT truck-mounted and tailgate-hung deicing tanks. The distribution system will be capable of filling and emptying all styles of truck tanks as well as recirculating fluid in the bulk storage tank to reduce chloride solids settling.

Brine Making and Distribution System:

Brine making system or the infrastructure for a brine making system may be requested. The brine system will provide fully automated, on-demand production and include a salt hopper, water and brine storage tanks, fluid distribution and additive injection system, and digital controls. The standard system is an AccuBrine ABS2 as manufactured and installed by Cargill, Incorporated. This system exists at the Wethersfield Maintenance Facility.

Infrastructure requirements include a secured space in the bay area for a control panel (approx. 12’x8’ min.), adjacent single bay for salt hopper storage and usage, adjacent exterior concrete pad for polypropylene above-ground storage tanks, as well as plumbing, pneumatic and electrical components installed within the building. Water supply will consist of a 2” home-run line with backflow preventer terminating near the control panel. A ½” compressed air line for tank purging will be provided. A receptacle providing 208V at 30A, 3ph will be located within 5’ of the control panel. Conduit runs are required from control panel area to storage tanks and remote truck fill station.

MS4:

A Department MS4 Mediation team is currently working with CT DEEP to develop a DOT Separate Storm Sewer System General Permit (DOT MS4 General Permit) - effective date still to be determined.

Existing Maintenance facilities are exempted from coverage for their activities under the DOT MS4 General Permit due to their separate coverage under the CT DEEP’s Stormwater General Permit for Industrial Activity  issued under same authority as for MS4 (22a-430b).

For new construction, redevelopment and restoration activities the Department’s goal shall, to the maximum extent practical, be to develop designs that minimize IA (impervious area) and DCIA (directly connected impervious area) consistent with the CT DEEP’s Construction Stormwater General Permit (regardless of the proposed area of disturbance).

DEMOLITION

The following demolition guidelines are offered:

Complete Buidling Demolition

On projects involving the complete demolition of a building or buildings, only a Site Plan is required to be prepared with demolition call-outs.  Each Designer shall provide the Civil Designer with the necessary salvage requirements.

Selective Building Demolition

On projects involving the selective demolition of a building or buildings, the following plans are required:

Civil Demolition Plans

Tank Demolition Plans

Architectural and Structural Demolition Plans

Fire Protection Demolition Plans

Mechanical and Plumbing Demolition Plans

Electrical Demolition Plans

Designers shall include a clear description of salvage and demolition work on their plans.  New work should not be described on the demolition plans.  Designers shall review the demolition plans of other Designers to clearly describe the scope of new work.  Extra work has been paid to Contractors when this coordination does not happen.  For example, if the mechanical demolition plan removes a roof fan the structural work plan needs to include a deck in-fill detail.  The structural plans should have general notes directing the Contractor to in-fill all existing holes in the walls generated by the removal of materials from various demolition plans.

Special Note

If the bay areas of an existing building are to be renovated, closely examine the condition of the overhead door sill angles, slabs, and roof deck to identify areas to repair.

ARCHITECTURAL AND STRUCTURAL PLAN DEVELOPMENT

GEOLOCATION OF PLANS

Coordinate with the Civil Designer to geo-locate the architectural and structural plans early in the project development.  The Civil Designer will need to verify the accuracy at 90%.

GENERAL PLAN DEVELOPMENT

Plans will bear dimensions that are reckoned from centerlines (of walls, column lines, or grid lines).  That is why grid lines are very important as points of common reference, and shall be established at the get-go on the building floor plans.  Dimensions shall not be referenced from “out-to-out” points because the materials that we use for building envelope, i.e. CMU and bricks do not have absolute, perfect and consistent widths, lengths and heights.

For Architectural plans that need to establish actual inside/outside dimensions of rooms and spaces, these dimensions could be shown as “out-to-out” or “in-to-in” of such rooms and spaces in the detailed/blown-up plans.  These dimensions could then be noted as “approximate” due to the variances in the wall/CMU/brick thicknesses.

Where applicable, wall sections should be identified with their UL wall assembly number.

Both floor plans and site plans need to indicate finished floor elevations in the same units (feet or feet-inches).  The floor plan elevations should be the high point elevation and be noted as same.

A draft copy of the International Building Code Plan Review Record and the ANSI A117.1 Plan Review Record will be submitted with the Preliminary Design (30%) submission for review.  This will ensure that the floor plan complies with the respective codes.

The Project’s Structural Designer will design and detail all structural support systems and their appurtenant connections as opposed to leaving this task to the sole discretion of the Contractor’s Designer.  The Structural plans will depict framing plans and details for all concrete or steel deck penetrations including, but not limited to, the following: mechanical equipment, roof drains, hatchways. The building structural support system shall include the supports for appurtenances such as mechanical and electrical equipment, and architectural components that require permanent attachment.

GENERAL

The building will be steel-framed in combination with load-bearing and non-load-bearing concrete or masonry walls.  The roof diaphragm will be steel deck supported on steel truss joists.  The minimum clear height to the bottom of steel (joists, beams, or crane rails) in the Bay Areas will be 19’-9”.  This height needs to be verified early on with the equipment list.  A triaxle truck needs 3-feet of additional clearance to install the correct overhead/sectional doors.

CODE CONSIDERATIONS

Employee Rest Break Options

The Project Engineer and the design team shall determine which option the design will pursue.

The area with Use Group B where employees take rest breaks for 10 or fewer employees is classified as R-3 and is classified as R-1 for more than 10 employees.

- Rated Separation between Use Group B (R) and S-1 with Fire Suppression System:

Separation between Occupancies R and S-1 or B is 1 hour sprinklered in accordance with the 2015 IBC Table 508.4 (design for 2 hours if feasible).  Also need to comply with 2015 IBC Section 420 and 508.3.3 also point out fire separation for R Use areas.  Employees can rest in any location within any office, Conference Room, or Break Room.  This shall be considered the design standard for the typical project since it is the easiest and most generous approach for sleeping arrangements.

- Rated Separation between Use Group B (R) and S-1 without Fire Suppression System:

Separation between Occupancies R and S-1 or B is 2 hours non-sprinklered in accordance with the 2015 IBC Table 508.4.  Also need to comply with 2015 IBC Section 420 and 508.3.3 also point out fire separation for R Use areas.  The Conference Room shall be provided with a direct exit outside.  Employees can rest only in the Conference Room.

- Unrated Separation between Use Group B (R) and S-1 with Fire Suppression System:

A 2 hour separation shall be constructed around the Conference Room.  The Conference Room shall be provided with a direct exit outside.  Employees can rest only in the Conference Room.  This should be considered a last resort option likely encountered on a renovation project where the existing wall ratings are unknown.

- Use Group S-1 with Fire Suppression System:

Where the office area is less than 10% of the overall area, fire separation is exempt and not required.  Employees can rest in any location within any office, Conference Room, or Break Room.

Fire Areas:

Comply with the 2015 IBC Table 707.3.10 – but note the higher required rating) and the 2015 IBC Table 506.2 that shows a huge difference in square footage allowed for a Type IIB building (typical facility) when sprinklered and non-sprinklered.

OFFICE AREAS

The office layout of a maintenance facility needs to have a combination of shared and private offices.  The quantities and types of offices are dictated by the Scope Questionnaire for the particular facility.  Private offices include, but are not limited to, the following: Clerk, Crew Leader, Supervisor, and Manager.  Private offices are typically sized for 250 SF/person with additional area for furniture (including couches in Supervisor Offices) and wardrobes unless closets (with or without shelves) are provided.

Private offices are typically located on exterior walls along the front of the building.  Unless requested otherwise, Clerk offices will be adjacent to the main entrance Vestibule with a fixed window to provide visibility into the vestibule.

Four occupant loads will be considered when designing the facility: current male employees, current female employees, additional employees to fully staff the facility, and additional employees for winter storm operations.

Break Rooms are required and will be large enough to accommodate all facility employees. Based on the latest State of Connecticut Building Code Table 1004.1.2 for “Assembly – Un-concentrated tables and chairs”, a minimum of 15 SF/person will be allocated.  The Break Room will include the following: a refrigerated water cooler, kitchen-style cabinets, a kitchen-style sink, a refrigerator, a microwave, and 220V stove.

Halls are required to permit the movement of the facility occupants throughout the facility without going outside.  The main entrance(s) will include vestibules.

Conference Rooms are required, and will be large enough to accommodate 1/3 of the facility employees resting at a time.  Based on the latest State of Connecticut Building Code Table 1004.1.2 for “dormitories”, a minimum of 50 SF gross/person will be allocated.  Conference Rooms will have exterior personnel doors with no exterior door hardware.  Include power/voice/data at 3 locations for future training stations.

Separate male and female bathrooms (full height walls) and locker rooms will be provided.  Male locker rooms are typically adjacent to the restroom while female locker rooms are typically included within the restroom.   Built-in lockers 18” x 18” x 60” will be provided for each employee permanently or temporarily assigned to the facility, however, the female locker room will include a minimum of 10 lockers (verify with Design Project Engineer).  Minimal plumbing fixture counts for water closets, urinals, showers, and lavatories are dependent on the requirements of the State of Connecticut Building Code; however the actual number of fixtures will be inflated based on the common employee work day.

Other spaces include:

1.	Janitors’ Closet: Full height walls with suspended ceiling.  Include floor sink

2.	Cot Room: For office supply and cot storage.  Verify with occupants which style of cots they have: 36” wide by 48” high by 16” deep or 34” wide by 34” high by 8” deep.

3.	Mechanical Room: Will be sized by the Project’s Mechanical Designer and will typically feature exterior double doors

4.	Sprinkler Room: Will be sized by the Project’s Mechanical Designer and will typically feature an exterior door

5.	Electrical and Communication Rooms: Will be sized by the Project’s Electrical Designer in accordance with Appendix 1 for the “Electrical/Communications Room Design Criteria.”  Electrical Rooms will typically feature an interior door to maximize the exterior wall space and the Communication Rooms will typically feature an interior door from the Electrical Room.

6.	Secondary Communications Closet: A centralized communications closet will be included to meet the Department’s current and projected IT needs.

TYPICAL VEHICLE DIMENSIONS AND BLOCK HEATER REQUIREMENTS

Refer to Appendix 4.  Verify actual vehicle storage needs with occupants.

BAY AREAS

If the site permits, the facility generally has half the bays on each side of the office area. Since the mechanical equipment is located in the office area, this type of layout makes for an easier piping layout.  Drive-thru bays are preferred barring any site restrictions.

The standard size truck bay is 15-feet wide by 50-feet deep with 14-foot wide by 16-foot tall overhead doors.  Oversize bays are provided as needed for egress doors, and for specialty/wash/weld bays.  These bays are typically a minimum of 20-feet wide although they may be 26.5-feet wide to accommodate a 10-wheel double wing plow truck.  Overhead doors will be 18-feet or 20-feet (for the double wing) wide by 16-feet tall.  A fiberglass catwalk installed 11’-8” AFF spanning the majority of the Wash Bay depth shall be included in the Wash Bay if the facility has or may ever have a triaxle plow truck.  The catwalk shall be a minimum of 36-inches wide between the handrails and the stairs shall be a minimum of 32-inches wide between the handrails.

Ideally, 2 side-by-side Wash Bays are required at each facility.  This Wash Bay will have doors separating it from the rest of the facility.  All walls will be glazed block to a height of 12-feet AFF.

Where possible, tube steel between overhead doors shall be a minimum of 16-inches wide to accommodate the FMG- compliant overhead door tracks along with the overhead door controls and electrical receptacles.

Tool and storage (including small oxygen and acetylene) cribs will be sized and located where requested by the owner/occupant.  Each crew typically has its own tool crib.  Shelving systems will be included as requested by the owner/occupant.

In-slab secondary containment detention basins sized for the storage of 55 gallon drums and smaller containers will be sized and located where requested by the owner/occupant, unless they prefer to continue to use the existing aboveground secondary containment basins.

EXTERIOR ELEVATIONS

The typical appearance of the exterior elevations will be for the Office Area to be constructed with a lower roof line out of split-face and ground-face block.  Typically the colors will be earth-tone.  The Bay Areas will be constructed out of this same split-face and smooth-face block to the top of the personnel door frame.  Above this elevation the building will be insulated metal siding typically in an earth-tone color.  Brick is also used.

Provide a ladder through the roof hatch in the Mechanical Room or anchored to the exterior of the building.  Any exterior ladder from grade will require a safety cage with a locking gate.  Install exterior ladders between the various roof levels.  Include a safety cage around the roof hatch.

INTERIOR ELEVATIONS

The following walls will be full-height masonry:

- Fire-rated walls including, but not limited to, the following: Halls, Vestibules, Mechanical Room, Sprinkler Room, and the separation walls between the Office and the Bays.

- Electrical and Communication Rooms.

- Janitor’s Closets.

- Compressor Rooms.

- Female Bathrooms.

The following masonry walls will extend a minimum of 8-inches above the ceiling:

- Office walls, including Office closet walls.

- Walls between the Men’s Room and the Men’s Locker Room.

- Break Room.

- Conference Room.

- Other rooms such as Cot Room and Media Storage Room.

With the exception of limited uses identified elsewhere, gypsum walls will not be used without the approval of the owner.

Interior walls will close with exterior walls to ensure that there are no gaps to transmit noise, water, and air between the spaces.  If concealed above a ceiling, shaft wall may be used if structural framing members are in conflict.

Where appropriate, walls within the facility should be identified with their UL Rating to ensure they are properly constructed.

COLOR SELECTIONS

During the Design process, the Designer shall work with the building occupants and owner to determine a color scheme for the applicable (particularly architectural) materials.  This color scheme can then be included in the Contract specifications, and by doing so will simplify the Contractor’s submittal process.  The Designer shall work with the building owner to standardize color selections wherever possible.

CSI DIVISION 3 – CONCRETE

Compressive Strength for Cast-in-Place Concrete:

Cast-in-Place Concrete shall be Class F – Normal Weight, with a minimum Compressive Strength of 4,000 psi. at 28 days.  The Class F designation shall be on the plans.

Investigate the use of low permeability concrete to help keep the chlorides away from the rebar.

Reinforcing Bars:

Reinforcing Bars shall be Deformed Billet Steel, Grade 60 conforming to ASTM A615.

Welded Wire Reinforcement shall conform to ASTM A185.

Reinforcing Mesh:

Past projects specified 6x6-W6.3xW6.3 epoxy-coated mesh, but this is apparently an uncommon size.  Epoxy-coated WWF 4x4 W4/W4 has been.

Non-Shrink Grout:

Non-Shrink Grout shall have a minimum Compressive Strength of 6,000 psi.

Vapor Retarder:

This vapor-retarder sheeting (of 15 mils in minimum thickness) will cover the top of the granular fill on the underside of the slab-on-grade to deter the migration of vapor/moisture from the soil into the concrete slab.

CSI DIVISION 4 – MASONRY

Compressive Strength of Concrete Masonry Units (fm):

Concrete Masonry Units (CMU) shall be Type I – Lightweight, with a minimum Compressive Strength (fm) of 1,900 psi at 28 days.  Hollow Block Units shall conform to ASTM C90.  Solid Block Units shall conform to ASTM C145.

Due to concerns with rebar and grout installation do not use 4-inch CMU unless there is a special case where rebar and grout installation are not a concern.

Grout:

Grout shall conform to ASTM C476 with a minimum Compressive Strength of 3,000 psi.

Mortar:

Mortar for Block Units shall be Type S conforming to ASTM C270 (f’m = 1,500 psi).

Mortar for exterior Block Veneer shall be Type N conforming to ASTM C270 (f’m = 1,350 psi).

Split-Face and Ground-Face Block:

These blocks will be used on the exterior elevations.  Color will be brown and tan with grayish-tan grout.

Glazed Block:

Glazed block will be used in Wash Bays.  Color will be off-white or tan with grout to match.

Pre-Cast Window Sills:
Pre-cast window sills will be grayish tan.

CSI DIVISION 5 - METALS

Structural W-Shapes:

Structural W-Shapes shall be 50 ksi steel, conforming to ASTM A992.

Hollow Structural Sections (HSS):

Hollow Structural Sections shall be 50 ksi steel Grade C, conforming to ASTM A500.

Structural Angles, Channels and Plates:

Structural Angles, Channels and Plates when used as secondary structural elements may be 36 ksi steel, conforming to ASTM A992.

Bolted Connections:

Bolted connections shall be “Slip-Critical” using ¾”-Diameter Pre-tensioned or Tension-Control A325 High-Strength bolts.

Welded Connections:

Welded Connections shall be performed in accordance with AWS D1.1 using E7018 Electrodes.

Steel Joist Framing:

Steel Joists shall be designed and installed in accordance with the SJI Standard Specifications for Steel Joist Construction.

Steel Deck:

The Structural Designer shall coordinate with the Architect to ensure that the steel deck and roofing system design will comply with FM Global Data Sheets and the Building Code.

Steel deck shall be manufactured and installed in accordance with the SDI Specifications for Composite Decks, Form Decks, Roof Decks and Cellular Metal Floor Deck with Electrical Distribution.

Typical steel deck shall be a  1 ½” Wide-Rib 18 Gauge Steel, Type B, with a minimum Yield Strength of 33 ksi and complying to ASTM A446.

Steel Deck shall be galvanized in accordance with ASTM A525, Coating Designation G90.

CSI DIVISION 6 – WOOD, PLASTICS, AND COMPOSITES

Catwalk:

For facilities that has or may ever have a triaxle plow truck, a fiberglass catwalk will be installed in the Wash Bay, spanning the majority of the bay depth and will conform to OSHA standards. All components will be fiberglass reinforced plastic products to protect it against water and salt erosion. The catwalk will be installed 11’-8” AFF to the walking surface, and have a minimum of 36-inches between the handrails. The fiberglass stairs ascending to the catwalk will have a minimum of 32-inches between the stair handrails. Color of gratings and railings will be Yellow, and color of structural elements, frames and supports will be Gray. Catwalk will be freestanding, with supports only into the slab below.

Electrical Backboards

Where required, electrical backboards shall be 3/4” fire retardant plywood, treated on all sides, and sized based on amount of equipment required.  Backboards will be painted black on all sides unless located in a finished office, in which case they will be painted to match the walls.

CSI DIVISION 7 – THERMAL AND MOISTURE PROTECTION

Bituminous Dampproofing:

This vapor-retarder compound is applied on the entire outside face of perimeter concrete foundation wall, including the outside top of footing, and continues to a minimum of 6” down its outside face to protect against dampness.

Water Repellents:

This coating is applied as a penetrating finish and protectant to horizontal and vertical surfaces.  Horizontal surfaces include all Wash Bay, Bay Area, Mechanical, Sprinkler, Electrical, and Communication Room slabs.  Vertical surfaces include exterior block and brick.

New exterior concrete including, but not limited to, pads, slabs, fuel Island and tanks needs to be protected from salt for the first year.  Saltguard WB as manufactured by Consolideck has been used on past projects.

Thermal Insulation:

Rigid insulation is installed above the metal roof deck and within the exterior cavity wall at thicknesses required by current code standards. Two inches of rigid insulation is installed at the vertical and horizontal perimeter of the concrete slab.

Metal Wall Panels:

Panels are insulated (currently 3” thick) to meet the current code standards, exterior color will be tan and interior color will be white.  Metal wall panels are installed in the bay areas above the personnel door frames.

Roofing:

The Architect shall coordinate with the Structural Designer to ensure that the steel deck and roofing system design will comply with FM Global Data Sheets and the Building Code.

The typical facility roofing system will be a single-ply PVC roofing system, 80 mils, and color white. System includes 3 foot wide walk pad to provide access to roof top equipment including roof drains. An alternate for buildings with sloped, guttered roofing systems that do not have air conditioned spaces is single ply EPDM roofing membrane, 60mils, and color black. Both roofing systems will require the same 20 year No Dollar Limit Warranty.

The roof shall be mechanically fastened on metal decks and fully-adhered on concrete decks.  Adhesives shall be low VOC.

The plan sheets, instead of the specifications, shall include a detail for the Roof Warranty sign.

Roof Accessories, Roof Specialties, and Sheetmetal Flashing and Trim:

Accessories include a 3’-0” x 2’-6” roof hatch located above and accessed from the Mechanical Room, installed with the walkway a minimum of 10’-0” horizontal distance from the roof edge.   Roof hatch will include a safety railing.  Railing will be yellow.  Remaining materials will match adjacent materials.

Expansion Control:

Joint expansion systems may be required to accommodate anticipated structure movement depending on the size and construction of the building. The Project Architect and Structural Designers will coordinate to determine if required.  Interior will be paintable to match the walls and the exterior will be tan to match the masonry and siding.

CSI DIVISION 8 – OPENINGS

Hollow Metal Doors and Frames (Personnel Doors):

Exterior doors will be Level 3 and Physical Performance Level A (Extra Heavy Duty), insulated.  Interior doors will be Level 2 and Physical Performance Level B (Heavy Duty).  All doors will be reinforced for hardware.  Include half-lite doors at the main entrance, inner vestibule door, and office doors, break room doors, and conference room doors.  Include narrow type vision lites on the lock side of all doors except where specifically prohibited by code or where vandalism is an issue.  Include solid doors at Bathrooms, Locker Rooms, Janitor’s Closet, Mechanical, Electrical, Communication, and Sprinkler Rooms.  Full glass doors will not be installed. Color will be dark brown.

Aluminum storefront systems will not be installed without the Owner’s approval.  The heavy salt conditions have caused aluminum to decay and also the threshold-mounted pivot to seize, so an alternate hinge is required.  Color will be dark bronze.

Coiling Counter Fire Doors:

Coiling counter fire doors will be installed where required by code at windows in fire-rated assemblies.

Overhead Doors (Coiling Doors and Sectional Doors):

Sectional doors are preferred, although coiling doors shall be installed to avoid interference with overhead cranes and vehicle lifts only if necessary.  Sectional door rollers and tracks will be 3” style. Basic door design is an insulated-style door with a thermal core.  For sectional doors, dark brown is the preferred exterior color with white as the interior color subject to architectural consideration.  For coiling doors, dark brown is the preferred exterior and interior color subject to architectural consideration. Typical sectional doors shall have standard lift tracks unless the design requires high lift tracks for vehicles such as triaxle trucks and other elements such as existing conditions and cranes.  Standard lift sectional doors are required to have trolley operators. High lift sectional doors and coiling doors are required to have side-mounted jack shaft operators and provisions for emergency manual operation. High lift sectional doors are required to have safety exit devices. All overhead door operators shall be wired so that the doors will be closed by continuously holding the “close” push-button.  Pass doors in the overhead doors are not desirable for safety reasons.

Windows:

All exterior windows will be 5’-0”H x 6’-0”W dark bronze aluminum.  Office windows will be located at an elevation to permit employees to look out the window from a seated position.  Windows are not typically installed in Bay Areas.  On renovation projects, Bay Area windows will be removed and the opening in-filled.

One interior 4’-0”H x 3’-0”W steel window, painted to match the doors and frames, will be installed in the Vestibule/Clerk’s Office wall. This window will be fire rated to match the Vestibule walls.

Door Hardware:

The CT DOT has a Statewide Key System.  These locks are usually not stock items and have been the subject of much confusion over the years.  All locksets and panic hardware must accept Master Ring diameter cylinders.  All cylinders must also be able to accept small format 7 pin interchangeable cores.  In the case of exit devices, the only device allowed is the push bar style.  Corbin-Russwin does not make a push bar style that will accept Master Ring style small format interchangeable core housings.  The companies that make push bar exit devices can modify their trim to accept Master Ring Cylinders.  It is critical to follow the latest Door Hardware CSI Section exactly.  Private offices will be capable of being locked.

The inner Vestibule door frame will be prepared for a fire rated electric strike that will be controlled by a push button door release button in the Clerk’s Office.  Doors between different occupant bay areas will be capable of being locked.

A “Knox Box” will be installed if the municipality subscribes to the program or an equivalent program.  On sites that are fully fenced, the “Knox Box” will be mounted on the gate; otherwise the “Knox Box” will be wall-mounted outside the main office entrance unless an alternate location is requested.

Glazing:

Monolithic clear/transparent, non-wired glazing will be provided at all exterior and applicable interior doors and at clerk room window. Insulating glazing units will be provided at all exterior windows. Glazing at exterior windows and doors will be tinted green and heat strengthened. Safety glazing will be provided at all doors and fire rated glazing will be provided when door and window is located in a fire rated wall.

Louvers and Vents:

Two louvers will be provided at the exterior wall of the Mechanical Room and sized based on the free air required as determined by the Mechanical Designer and located by the Architect in compliance with the Building Code.  Color will match the exterior windows.

CSI DIVISION 9 – FINISHES

Non-Structural Metal Framing:

Metal framing will be provided behind the tiled cement board wall adjacent to the shower enclosure unit to accommodate ADA clearance requirements for wheelchair seat transfer; framing will also be provided above to enclose unit. Metal framing and gypsum wall board may also be provided above and behind break room cabinetry to accommodate mechanical plenum and soffit above upper cabinetry.  No magnesium oxide is permitted in the sheet rock.

Tiling:

Ceramic tile will be provided on metal framed cement board walls around shower enclosure unit, color will be off-white.

Acoustical Tile Ceilings:

Acoustical tile ceiling will be provided at all office core locations except at the mechanical and electrical rooms. Tile ceiling rated for wet locations will be provided in the Bathrooms, Locker Rooms, and Janitor’s Closet.  Color will be white.

Flooring:

Unless otherwise noted, flooring in the finished Office Area spaces will be cementitious (polyacrylate modified) terrazzo flooring with epoxy terrazzo base. The selected color will be darker to better hide the dirt.  Suggest Occum and Pomfret as a basis-of-design with a gray tone color.  Epoxy terrazzo flooring will not be used due to past issues with unacceptable slab moisture levels when a moisture mitigation system was not included. When requested by the Owner/occupant, dark brown NORA flooring will be installed in the individual offices.  In this case, the flooring in the Bathrooms, Locker Rooms, Janitor’s Closets, Vestibules, and Halls will be epoxy.

The flooring in the Wash Bays, Bay Areas, Shops, Mechanical Room, Sprinkler Room, Electrical Room, and Communications Room will be sealed concrete.

Painting (Interior and Exterior):

All visible spaces will be finished.  Walls will be painted an off-white color in the Office Areas and in the Bay Areas, except in Repair Bays the walls will be painted a darker color to the top of the door frames.  All structural steel, joists, girts, and sub-girts, steel around bay doors, steel doors, steel windows, and steel frames will be painted dark brown. The metal deck will not be painted.  With the exception of sprinkler piping which will be painted red and gas piping which will be yellow, any uninsulated piping and conduit will be painted to match the adjoining surfaces.

The Contract needs to reflect the new DEEP VOC limits for field-applied paint.  These provisions do not apply to shop-applied paint if the painting occurs outside of CT.

CSI DIVISION 10 – SPECIALTIES

Visual Display Surfaces:

Visual display surfaces are installed in Offices, Conference Rooms, and Break Rooms where directed by the owner/occupant.  Color will be light gray.  Contract shall be written so that the visual display surfaces are installed by the Contractor after the Owner furniture is installed (typically this means a Punch List item).

Signage:

Signs will be installed at each interior personnel door.  Exterior signs are not required.  All signs will comply with ADA requirements.  Signs will be dark brown with white letters and painted stencils will be white.

Toilet Compartments:

Toilet partitions will be phenolic core floor anchored and overhead braced metal with a baked enamel finish.  All panels will be minimum 20-gauge with 22-gauge doors. Color will be earth tones.  All hardware shall comply with ANSI A117.1 for handicapped accessibility.

Tool Cribs and Storage Cribs:

Tool and storage cribs will be constructed from chain link fence components. The walls will extend to within 18” of the bottom of steel to minimize the likelihood of someone climbing the wall to get into the crib or have sloped tops to prevent storage on top.

All tool crib gates shall include 2 ring bolts instead of the standard locking hardware.  These bolts shall be set to accept a state-furnished padlock.  Continue to use the drop rods on double-leaf gates.

Toilet and Bath Accessories:

The Department has standardized paper towels as 8” wide roll-style.  Paper towel dispensers will be installed in the Bathrooms, the Break Room, the Janitor’s Closet, and at each wash fountain.  The Department has standardized toilet paper as a full 12” diameter roll with a roll stub, Scott #07202.  The Women’s Bathroom will have a sanitary napkin dispenser, which vends both tampons and pads at 25 cents each.  Tilted mirror is only required when 40” ADA clearance mounted height above finished floor is not feasible.  Grab bars will be provided in accordance with ADA requirements.  Shower curtain will be white and toilet paper dispenser will be light gray.

Fire Extinguishers:

Unless otherwise required by the hazard, multipurpose Dry-Chemical Type in Steel Container:  UL-rated 4A:60-B:C, 10-lb nominal capacity, with mono-ammonium phosphate-based dry chemical in enameled-steel container fire extinguishers will be specified.  A UL-rated Class 2-A:K type fire extinguisher will be installed in the Break Room.  No fire extinguisher cabinets are desired inside the building.  A rust-resistant cabinet will be installed at the fuel island.  Include a quantity of fire extinguishers in the specifications but do not show them on the plans.  The plans will identify the locations to install the fire extinguishers in accordance with NFPA 10 with a note to coordinate with the authority having jurisdiction, in conjunction with CT DOT Safety, during construction.

Metal Lockers:

Single tier lockers and benches will be furnished, including marked ADA lockers. ADA compliant benches will be provided for handicapped lockers.  Doors to be minimum 16-guage steel with top and bottom minimum 24-gauge steel. Lockers shall be vented so as not to require louver vents in each door.  Key locks to be grooved key 5 PIN cylinder with spring bolt action.  All lockers shall have continuous sloping tops.  Metal lockers will be light gray.

Metal Storage Shelving and Workbenches:

Metal storage shelving and workbenches will be provided as requested by the owner/occupant.  The separation distance between shelving shall be 5-feet to permit forklift usage. If specified, double-sided steel racks shall not be proposed against a wall.  The workbenches shall be a minimum of 6-feet long and include a wood top.  A minimum of one workbench shall be provided for each crew within the facility.  Color will be manufacturer’s standard.

CSI DIVISION 11 – EQUIPMENT

Vehicle Service Equipment:

Fluid distribution systems and floor anchors are included in CT DOT Repair Facilities.

The fluid distribution system consists of storage tanks and drums with compressed air pumps located in a dedicated room conveying the fluids through a piping network to overhead hose reels with dispensers throughout the Repair Bays.  The hose reels are provided for various fluids serving vehicle maintenance and repair needs such as engine oil, antifreeze, transmission fluid, chassis grease, and compressed air.  No later than the preliminary design phase, Design will consult with facility Repair personnel to determine the system design parameters.  The dispensers should be located towards the front of the bays oriented towards the vehicles.  All system components will be rated for pressures of the fluids they are serving.  The system will be in compliance with applicable FM Global standards for containment underneath the fluid drums and fire safety measures in the fluid lines.

Concealed floor anchors are provided in Weld Bays for automotive tie-down and frame straightening.

Vehicle Washing Equipment:

A power washer will be provided in each separate Wash Bay.  The power washer will be suitable for the use of either hot or cold water and be mounted on a mobility cart with wheels and a handle and will include 50 feet of hose with rack and a power cord with plug.  Special receptacles will be provided in the Wash Bay for power.  The power washer will not be overhead or wall-mounted and will not include a hose reel.

Appliances:

A refrigerator with icemaker, a microwave oven, and an electric stove and plenum will be installed in the Casework.   Color white.

CSI DIVISION 12 – FURNISHINGS

Casework:

Oak kitchen cabinetry with a laminate countertop with backsplash and finished edges will be provided in the Break Room and will include upper and lower cabinets. The sink section of the countertop will be adjustable for ADA compliance.  A toe kick will be provided at the base to accommodate handicap accessibility. Color will be chestnut.

Horizontal Louver Blinds:

Provide manually operated 2-inch horizontal aluminum blinds for all exterior windows and for all interior windows and interior half-lite office doors.  Color will be light gray.

Furniture:

Furniture is not provided by the Contract.  Staff Maintenance is developing standards for what they will order based on the number and types of offices, conference rooms, break rooms, etc.  Love seats are also being provided in Supervisor and Manager Offices.  Refer to Appendix 2.  Furniture may limit the ability to install closets in some office spaces without enlarging the space.  Furniture will be paid for out of Project Contingencies.

CSI DIVISION 13 – SPECIAL CONSTRUCTION

Motor Fuel Island:

The Office of Property & Facilities Services and the Office of Fuel Control will determine if the facility will have both diesel and unleaded or just diesel fuel.  Storage tanks will be sized based on historical data.

The standard storage tanks will be UL 2085 protected aboveground storage tanks (AST’s). Tanks will include all applicable appurtenances for filling, vapor recovery, submersible pump, vents, and tank monitoring. Where site conditions don’t allow for ASTs, fiberglass, double-wall underground storage tanks (UST’s) will be provided. Tank construction, installation, clearances, and physical protection will comply with FM Global, NFPA 30, and NFPA 30A. Tanks will have a 30 year warranty.

Fuel inventory will be managed by a sole-sourced Fuelmaster 2500 Fuel Management Unit (FMU).  There is a sole-source approval memorandum on file.  The system works by reading information from a ProKee assigned to each vehicle. The system keeps track of all information related to the fill up including amount of fuel dispensed, vehicle odometer, vehicle ID, date and time, and hose number. The system will communicate all information to the Central Headend located at the CT DOT Headquarters in Newington via network connection.

Fuel dispensers will be electronic type, pedestal mounted, standard capacity, remote dispensers and super high capacity for high flow diesel. The dispensers will have color-coded product ID panels “Yellow” for diesel and “Silver” for unleaded. Nozzles will also be color coded.  For diesel fueling, at least one nozzle will be dedicated for high-flow fueling for larger capacity trucks to cut down on fueling time.  Two diesel dispensers will be installed to permit the simultaneous fueling of (2) trucks.  Higher traffic facilities may require more than one high-flow diesel dispenser.  All components for unleaded dispensing will be compatible with E85 Ethanol.

Standard equipment will include 1½” Schedule 40 black steel product piping painted gray, ¾ horsepower submersible pumps for unleaded and standard flow diesel and 2 horsepower submersible pumps for high flow diesel. Each submersible pump will have a normally closed solenoid valve that only opens when the pump is energized. Each product line will also have an emergency shutoff valve that closes via a fusible link in the event of a fire. Each product line will also have a pressure relief line to drain excess pressure back into the tank. Product hoses will be black rubber with ¾” diameter for unleaded and standard flow diesel and 1” diameter for high flow diesel. Hoses will include breakaways and spin on filters.

Power to the fuel island will be provided from a dedicated panel connected to a shunt trip breaker. Each submersible pump will have its own disconnect switch. Emergency shutoff pushbuttons will be provided inside the Clerk’s Office (unless directed otherwise) and on the exterior wall (or other code compliant location) nearest to the fuel island. An emergency phone with single pushbutton dial out to 911 capabilities will also be located next to the exterior emergency push button. Exterior lighting will be provided for the fuel island. Toggle switches for dispenser power, dispenser lighting, and island lighting will be located in the office. All fuel island conduits will have explosion-proof fittings per applicable codes and all intrinsically safe wiring will be separated. All electrical materials will be coordinated with the Electrical Designer.

Diesel Exhaust Fluid (DEF) Systems:

Each motor fuel island with a diesel fuel tank shall include a 500 gallon AST for the DEF fluid.  The basis-of-design shall be the Northern DEF-Pro All In One storage and dispensing system, as manufactured by Dennison Lubricants, Inc.

Tank Monitoring System:

Each facility will have a tank monitoring system to monitor all storage tanks on-site. The department has three (3) acceptable manufacturers that meet our specific needs. They are Pneumercator, Veeder Root, and Incon. The system will consist of a console and printer, along with in-tank probes, interstitial sensors, sump sensors, and tank overfill alarms as required. The system will communicate with the FMU and the Headend via network connections.

Motor Fuel Island Electrical:

All underground conduits installed under the slab and surrounding areas will be installed 24” below final grade. Underground conduit with at least 2 ft. of cover will be schedule 80 PVC and will transition to RGSC, 2 ft. before the point of connection to the aboveground raceway.

All conduit and junction boxes in the fuel island area will be provided with explosion proof fittings and sealed as required in accordance to NFPA 70. Rigid conduit extensions above ground within 20 ft. proximity of fueling will be terminated at 18 inches minimum above grade with EY fittings. This includes the conduits that enter the FMU.

Paint Spray Booth and Paint Blast Booth:

The basis-of-design for these booths is Global Finishing Solutions.  The contact information is:

Mike Nobes from GFS  715-533-8685

mnobes@globalfinishing.com

For general guidance, the Department will maintain (1) Paint Spray Booth per District and only (1) Paint Blast Booth (existing at Rocky Hill Repair).

CSI DIVISION 14 – CONVEYING EQUIPMENT

Vehicle Lifts:

Vehicle lifts will be provided at Repair Facilities.  Specifications for vehicle lifts will be based on products offered by Mohawk or Rotary Lift.  The type, capacity, and quantity of lifts will be determined on a project by project basis based on consultation with the Office of Equipment Repair.  Color is manufacturer’s standard.

Hoists and Cranes:

One 3 ton capacity (labeled 2 ton) electric monorail hoist crane is typically provided in maintenance facilities.  Crane shall be NEMA 4X if required.  Three (3) ton capacity electric bridge cranes are typically provided in Weld Bays and Repair Bays.  Type and quantity will be determined on a project by project basis based on consultation with the Office of Maintenance and the Office of Equipment Repair. Color is manufacturer’s standard.

CSI DIVISION 21 – FIRE SUPPRESSION

If city water is available, a sprinkler system will be provided.  The system will be either a wet pipe or dry pipe system.  Where incoming city water pressure is not adequate enough to meet the sprinkler demand, an air-cooled diesel-drive centrifugal fire pump will be installed to increase pressure.

Coordinate the sprinkler system design with the water company as they may have requirements for shock/surge or break tanks.

Fire Department connections shall be in accordance with the requirements of the local fire marshal.  The options are threaded 2-1/2” or Storz-type thread-less couplings listed for use as a fire department connection.  This is further outlined in General Information Notice 20110-01 that was issued by the CT Office of the State Fire Marshal.

Coordinate the floor plan design with the project Architect and Structural Engineer.  Unless approved on a project-by-project basis, the fire-resistive element requirements of the building such as fire area and wall ratings will not be lessened due to the inclusion of the sprinkler system.

Automatic Sprinkler System shall be provided throughout all buildings that include a Group R fire area except where there is an exit door directly to the outside at the level of exit discharge in accordance with the 2018 CT State Building Code Supplement Section 903.2.8 Exception 2.1.

CSI DIVISION 22 – PLUMBING

All equipment and piping will be labeled with flow direction arrows.

General-Duty Valves:

General-duty valves will be ball valves instead of gate valves, globe valves, etc.

Domestic Water Piping:

Domestic water piping will be Type K Copper, Type L Copper, PVC, or ductile iron.  Pro-press copper fittings will be permitted by the specifications.  The domestic water piping system will serve the plumbing fixtures, the boiler makeup water line, and specialty water lines such as brine systems.

Domestic Water Piping Specialties:

All backflow preventers will be the reduced-pressure-principle type. In addition to those required within the building, a backflow preventer will be installed on the public water service main into the building.

A point of use cartridge-type filter in the Mechanical Room or Janitor’s Closet will be installed for the single water line that feeds the handicap accessible drinking fountain and the refrigerator icemaker.  Based on discussions with the authority having jurisdiction, this complies with the 2003 ICC ANSI A117.1 requirement for dual height outlets.

A trap seal primer distribution system will be provided at the office area floor drains.

Hose bibs will be provided in the bay areas with metal wheel handles and integral vacuum breakers.  Wash Bays will also include hot water hose bibs and 1½” fire hose thread adapter for high flow water.  Include an additional 1½” fire hose tread fitting on each catwalk. No exterior hose bibs are desired.  Any existing exterior hose bibs or wall hydrants shall be removed.

Domestic Water Pumps:

All in-line circulators will use a one (1) piece coupling spring type.  Couplings that use multiple springs are not allowed.  Equipment colors will be manufacturer’s standard.

Sanitary Waste and Vent Piping/Storm Drainage Piping:

All drainage and vent piping will be PVC.  The minimum diameter for roof drainage and bay area drain piping will be 6” diameter to prevent clogging.  Bay area drain piping from the Wash Bay will exit straight out of the building with no changes in direction to reduce the possibility of hardened salt clogging the piping.

Sanitary Waste and Vent Piping Specialties/Storm Drainage Piping Specialties:

Floor drains will be installed in the bathrooms, Janitor’s Closet, and Mechanical Room in the office area.  Floor drains may be installed at emergency plumbing fixtures.  On new construction, bay areas will have 12-inch wide polymer concrete trench drains with catch basins and ductile iron grates installed. Catch basins will include a sediment bucket. Joints in trench sections need to align with control joints in slab to prevent trench cracking. Renovation projects will either have trench drains or Type C-L catch basins installed. The biodegradable vehicle wash soap breaks down resulting in a rancid odor.  Therefore, all water should be permitted to drain from the building.  The sand trap should be outside.

Boiler relief valves will discharge onto the Mechanical Room floor to allow the discharge to be noticed and for the water to cool down prior to entering the floor drain.  The IPC does not permit the discharge of water hotter than 140 deg. F directly to the drainage system.

Waste Holding Tanks/Oil-Water Separators:

Waste holding tanks and oil-water separators will be double-wall fiberglass.  Waste holding tanks are typically 4,000 gallons.  Where the oil-water separator will be connected to a sanitary sewer system, the capacity will be 1,000 gallons.  In some cases a sanitary sewer system is anticipated to be installed in the future.  In this case, the capacity of the oil-water separator will be 5,000 gallons so that it can be used temporarily as a waste holding tank.  Tanks will have a 30 year warranty.   Tank gauge chart will be framed and mounted in the Clerk’s Office.  Oil-water separators shall be designed for less than 1,000 gallons per day.

Line Striping Paint/Wastewater Storage System:

Signs and Markings facilities require a system to store the line striping paint/wastewater.  The basis-of-design for this system shall include the following elements:

1.	Snyder Industries 2,000 gallon cone bottom above ground storage tank outside the building.

2.	Snyder Industries 120 gallon chemical feed station inside the building.

3.	Verderair VA 20 metallic pump to transfer paint/wastewater from the inside tank to the outside tank through HDPE piping.

The system design shall minimize the amount of piping between the pump and the outside tank.

Compressed Air Piping:

Air drops will be installed in every other bay.  Air drops will contain isolation valves (maximum 60-inches AFF), filters, regulators, and lubricators.  An air drop will be installed in the Mechanical Room without the filter, regulator, and lubricator.  Unless otherwise requested by the occupant, 3/8” and ½” quick disconnects will be provided at each location.  Compressed air reels will be installed in lieu of or addition to air drops in Repair facilities and elsewhere as requested by the owner/occupant.

Packaged Air Compressors and Receivers:

Each facility will have a compressed air system with air dryer. Air compressors will be two-stage reciprocating piston-type with splash lubrication and integral aftercooler. Air dryers will be air-cooled, cycling type.   Equipment colors will be manufacturer’s standard.

Domestic Water Heaters:

Domestic hot water will be provided as necessary. For facilities with natural gas, fuel-fired tankless water heaters will be used. For facilities with fuel oil, storage tank water heaters with one facility-wide continuous hot water recirculation loop will be used. Storage tank water heaters will have a 10 year warranty.  Oil-fired water heater with its own oil lines direct to the oil tank. Equipment colors will be manufacturer’s standard.

Plumbing Fixtures:

All fixtures in the restrooms will be white vitreous china. Water closets will have an elongated bowl with an open front, black toilet seat and a 1.28 gpf flush valve. Wall-hung urinals will have a 0.5 gpf flush valve. Lavatories will have a 0.5 gpm flow rate. Service basins in the janitor’s closet will be floor mounted, white molded-stone with a 2.2 gpm flow rate. Kitchen sinks in the break area will be stainless steel with a 1.8 gpm flow rate. All lavatory and sink faucets will be chrome plated brass. Showers will be enclosed FRP color white with an integral dome light.

Water coolers will include the bottle filling option.

Bay areas will have foot-actuated terrazzo, manufacturer’s standard beige/off-white, semicircular wash fountains and emergency eye/face wash stations as required to meet operational needs.  Wash fountains do not need to be ADA accessible since there are accessible sinks on the same floor.  Eye/face wash stations will be located to cover each set of bays, ideally located adjacent to hazard areas.  Hazard areas include, but are not limited to, the following: bulk liquid storage area and the Wash Bay.  Eye/face wash stations are either supplied with domestic hot water from a pipe loop or from a dedicated point-of-use water heater. There is no maximum linear distance for eye/face wash locations.   ANSI Z358.1-2014 requires them to be located in an area where an injured worker will not take longer than 10 seconds to reach the unit. This would mean that they should be located approximately 55 ft. from the hazard. They must be in a well-lit area that is on the same level as the hazard and they should be identified by a sign.

CSI DIVISION 23 – HEATING, VENTILATING AND AIR CONDITIONING

All equipment, piping, and ducts will be labeled with flow direction arrows.

General-Duty Valves:

General-duty valves will be ball valves instead of gate valves, globe valves, etc.

HVAC Instrumentation and Control/Sequence of Operation:

All HVAC systems will be controlled by a centralized, web based software-driven, building automation system.  This system is the Tracer Summit, sole-sourced by Trane.  There is a sole-source approval memorandum on file.  System design will be coordinated with the Rocky Hill, CT Trane Office as this group, led by Mr. Alan Berard, is familiar with the system requirements. Include block heater relays to enable/disable exterior receptacles based on exterior temperatures.

Design to the following room temperatures/parameters:

- Bays and Shops: Heating = 70-75 BTUHR/SQFT, no cooling

- Repair Bays: Heating = 70-100 BTUHR/SQFT, no cooling

- Electrical Room/Sprinkler Room: Heating = 70-75 BTUHR/SQFT, no cooling

- Mechanical Room: Heating = 100 BTUHR/SQFT, no cooling

- Stores Stockroom: 70-100 BTUHR/SQFT, no cooling

- Weld/Wood Shop: 70-100 BTUHR/SQFT, no cooling

- Offices: As determined by heating and cooling load calculations

- Wash Bays: 70-100 BTUHR/SQFT, no cooling

- Paint Storage Buildings: Heating = 55 deg. F, no cooling

Fuel-Oil Piping/Natural Gas Piping:

The preferred fuel source is natural gas. Utilities usually offer two service pressures; either 6 in W.C. or 2 psi.  Two (2) psi service due to demand of larger commercial appliances. A line pressure regulator will be installed prior to the building entrance.

If natural gas is not reasonably available the fuel source will be fuel oil. Aboveground storage tanks (AST’s) are preferred and will be spaced close enough to minimize piping runs from the tank to the fuel burning equipment.  The tanks will be UL 2085 protected. Tanks will include all applicable appurtenances for filling, vapor recovery, submersible pump, vents, and tank monitoring. Where site conditions don’t allow for ASTs, fiberglass, double-wall underground storage tanks (UST’s) will be provided. Tank construction, installation, clearances, and physical protection will comply with FM Global, and NFPA 30. Tanks will have a 30 year warranty.   Tank gauge chart will be framed and mounted in the Clerk’s Office.

Fuel Oil System:

The fuel oil tank shall feed a day tank inside the building with an integral pump. The day tank pump shall feed a single piping manifold along the ceiling with branches to each appliance. All aboveground piping shall be schedule 40 black steel. In the case where USTs are used, underground piping shall be UL 971 flexible secondary piping within 4” access piping until transitioning to aboveground inside the building.

Waste Oil Disposal System and Waste Antifreeze Disposal System:

In Repair facilities, a waste-oil and a waste antifreeze disposal system will be provided. Each system will consist of a double-wall AST, a wall-mounted funnel, a suction tube, and compressed air pump to pipe the oil outside to the tank.

Water Side Systems:

The hydronic heating system consists of a minimum of two cast-iron boilers that operate on a lead-lag sequence. Each boiler will be sized for 2/3 of the total load.  Each section of the building will have its own hydronic zone so to minimize the effects due to a pump failure.  Expansion loops will be provided in bay areas or other large zones.  Each boiler and each hydronic zone will be fed from an in-line circulating pump. In-line circulating pumps will have a one-piece spring coupling. Couplings with multiple springs are not allowed. Equipment colors will be manufacturer’s standard.

Primary heat in the office areas will consist of a duct-mounted hydronic coil served by its own dedicated in-line circulating pump.   The hydronic coil will be sized for a minimum of 130 deg. F leaving air temperature.  Secondary heat will be provided via finned-tube baseboard radiation in the exterior rooms, convectors in the interior rooms, and cabinet unit heaters in the bathrooms and locker rooms, served by their own dedicated in-line circulating pump.  Finned-tube radiation and convectors shall not be located in close proximity to plumbing fixtures.  Finned-tube radiation and convectors will be color ivory.

Heat in other areas such as bays, specialty bays, stockrooms, mechanical rooms, electrical rooms, and sprinkler rooms will be provided by suspended hydronic unit heaters served by their own dedicated in-line circulating pumps for each area of the building. Equipment colors will be manufacturer’s standard.

In Repair Bays, radiant floor heating with its own in-line circulating pump will also be provided as directed on a project-by-project basis in the work stations.  Equipment colors will be manufacturer’s standard.

Air Side Systems:

The office area, including any vestibules, will be served by a packaged rooftop unit, manufacturer’s standard color, with economizer and associated supply and return ductwork. The system will be changeover bypass/VAV type.  Each room will be served by its own dedicated VAV. Occupied spaces will have demand control ventilation via carbon dioxide sensors.  Diffusers and return grilles will be white.

Ducts in bathrooms, locker rooms, and other project-by-project locations will be aluminum.  The remaining ducts will be galvanized steel.

Rooftop centrifugal exhaust fans will serve the bathrooms, locker rooms, Mechanical Room, Electrical Room, and bay areas.   Bay area fans will be provided in the facility sized to perform proper air exchanges in a diesel truck environment.  Fans shall be sized based on the Mechanical Code:

Water Closets/Urinals: 50 CFM each (continuous) or 70 CFM each (intermittent) *

Shower Head: 20 CFM each (continuous) or 50 CFM each (intermittent) *

* Historically a minimum of 200 CFM has been provided in each bathroom

Locker Rooms: 0.5 CFM/SF

Bays: 0.75 CFM/SF **

** Historically the Mechanical and Electrical Rooms have matched the Bays at 1.5 CFM/SF

Weld Shops shall be 2 CFM/SF minimum.

On a project-by-project basis, exhaust fan override control will be permitted on a limited number of Bay area fans for odor control.  All weld shops shall include this override control.

Bay areas will also have downdraft fans for air circulation and temperature de-stratification.

Repair Bays, Weld Shops, Electrical Repair Shops, and similar areas will have point of use industrial/vehicle ventilation systems.  Vehicle ventilation systems should be located towards the front of the bays instead of the back of the bays.  Hose reels shall be approximately 9-feet AFF.  Additionally, a portable welding filter cart will be included in the specifications.

Break Area electric stoves will have a Type II kitchen exhaust system with no fire suppression system.  Supply plenum for the kitchen exhaust hood shall be manufacturer’s optional air curtain with 12 inch width to minimize mixing with air in the space

Communications Room Air Conditioners:

The Communications Room will be served by a mini-split air conditioning system with low-ambient controls.  The mini-split will be monitored by but not controlled by the building automation system.  Equipment colors will be manufacturer’s standard.

CSI DIVISION 26 – ELECTRICAL

Utility Coordination

For projects requiring new electrical or telecommunications service, design shall coordinate requirements with the local utility service company.  The Contractor’s scope of work, as it relates to the service, shall be detailed in the Contract.  Coordinate all details and information with the utility company.  A site meeting is typically conducted with all utilities present (power and communication). During that time location of service entrance, location of transformer (if applicable), and the routing of the overhead/underground service is discussed. Typically underground is the preferred routing of the service conductors unless there is a design obstacle or underground service is cost prohibitive.  Typically, the Electrical Designer will ask for the requirements to provide service to 10-20 data devices. A representative from Information Systems will be invited to the utility meeting to facilitate required services.

Local cable companies such as Cox Communications or Comcast typically furnish and install the cable in a conduit furnished and installed by the Contractor. Typically a 4” conduit from the riser pole to the Communications Room is provided for future cable requirements. Design will add to the specifications the language required to pay the Cable company/Contractor for any work required and related to the installation of Cable from the street to the facility.

Typically, Voice/Data communications companies such as Frontier furnish and install the cable in a conduit furnished and installed by the State/Contractor. A 4” conduit from the riser pole to the Communications Room is provided for the Voice/Data communications requirements.

Enclosure

All enclosures and cabinets will be the hinged type and will be steel in the Office and Bay areas. Enclosure types as indicated below:

- NEMA 1 for Bay Areas, Mechanical Rooms, Sprinkler Rooms, Electrical Rooms, and Communications Rooms.

- NEMA 3R for exterior.

- NEMA 4X for corrosive/wet areas.

- NEMA 4 for damp locations

Power Conductors:

All power conductors shall be copper, stranded, rated 600V insulation and will be #12 AWG minimum. All feeder and branch circuits will have an equipment ground conductor included with phase wiring. All circuits will have separate neutral conductor from electrical panels. All conductors and transformer windings shall be copper.

The electrical plans will be responsible for the power wiring of the Building Automation System (BAS). All power for the BAS shall come from the same uninterruptable power supply that powers the BAS Headend.

The electrical installer will furnish and install #6 AWG ground conductor in ¾” RGSC from MDP ground bar to communication backboard. MC Cable will only be used for troffer lighting from the light fixture to the closest junction box in the office area. MC Cable will be fully sized, made of steel, and will be equipped with a green insulated copper grounding conductor.

Data/Communication/Special System Cable:

Power and communications conductors will be installed in separate conduit systems. Communications and special equipment conductors will be rated for 300V insulation or per manufacturer’s requirements. Telephone/Data conductors will be Category 6 with a yellow jacket. Telephone/data conductors will be installed with no splices. Telephone/data, fire alarm, video surveillance, and public address installed in trench will be suited for underground installation.

Conductors for each special system (fire alarm, video surveillance, public address, and telephone/data, base radio antenna, tank monitoring system, occupancy sensors) will be installed in their own conduit system. All power and fire alarm conductors will be installed in conduit in the entire building. The remaining systems will be installed in conduit in areas without a suspended ceiling and may be installed without conduit (supported with supports made for the application) in areas where there is a suspended ceiling.

Grounding and Bonding for Electrical Systems:

Grounding conductor shall be copper, stranded. Conductor insulation will be green in color for all interior and exterior grounding conductors. Insulation for isolated ground conductors will be green with yellow stripes. Copper grounding cable connections will be exothermic welded for underground/below grade connections. Bolted connections will only be acceptable for applications where the electrode or equipment requires periodic disconnection/connection.

The steel framework of the building will be grounded with a ground rod at the base of every corner column at a distance of not more than 60 feet apart throughout the perimeter of the building. Provide a counterpoise electrically connected to each ground rod and to each steel column. Bury counterpoise not less than 30 inches below grade and 36 inches from the building foundation. The water metallic pipe will be bonded and a jumper braided conductor will be used to connect each end of the water meter.

Ground rods will be copper-clad steel pointed, ¾ inch in diameter and ten feet long. Drive ground rods until tops are 6 inches below finished floor or grade.

All electrical equipment enclosures and all metallic parts of the installation, including structures, metallic conduits, wireways, frames, hand-rails, ladders, platforms, fence and metalwork will be bonded and connected to the nearest ground cabled. The grounding conductor will in no case be a system neutral or a current-carrying conductor.

Supplementary grounding in form of an electrode shall be installed for pole lighting and handholes. Handholes will be grounded with a ground rod and a #8 AWG bare, tinned-copper conductor. Bond all exposed metal parts such as inserts, cable racks, pulling irons, ladders, handhole cover, and cable shield within each handhole. Pole lighting will be grounded with a ground rod and a #8 AWG bare, tinned-copper conductor. Bond all exposed metal parts such as the pole and the pole’s handhole. Grounding of utility transformer will be per utility requirements. All grounding electrodes included but not limited to, metal underground water pipe, metal frame of the building structure, concrete cased structure, grounding ring, rod and pipe electrodes, lightning protection, will be bonded together to form the grounding electrode system.

Raceways and Boxes for Electrical Systems:

Minimum conduit size shall be ¾”. The raceway system will only be installed overhead. There will not be any below the slab raceway installation. Only utility raceways routed from the outside will be allowed under the slab.

Office Areas and Bays: Conduit will be steel.  Conduit will be installed in finished walls wherever possible. Conduit inside wall will be EMT. Exposed conduit will be RGSC up to 10 feet AFF and EMT above 10 feet AFF.

Wash Bays and Salt Sheds: Conduits will be corrosion resistant. Conduit will be concealed in finished walls wherever possible. Conduit inside walls will be EMT. Exposed conduit will be PVC coated RGSC up to 10 feet AFF and Schedule 40 PVC above 10 feet AFF.

There will be no exposed cable in the Bay Areas, Wash Bays, or Salt Shed.

Use FMC for flexible connections to motors. Motors in wet locations will be fed by LFMC. Maximum length will be 6 feet from the junction box to the motor. LFMC will be equipped with a PVC jacket. FMC will be zinc-coated steel.

Conduit Fittings:

PVC coated RGSC fittings will be the threaded type and will be made of steel. RGSC fittings shall be the threaded type. EMT fittings will be the compression or screw-in type. Cast fittings will be made of steel or malleable iron. Metallic conduit bodies will be made of steel or malleable iron.

Raceway Boxes:

Wireways will be used for ease of installation when a large number of conductors are grouped together. The electrical installer may consider wireway installation in the Mechanical Rooms, Sprinkler Rooms, Electrical Rooms, and Communications Rooms. Wireways installed will be the hinged type. Exterior mounted wireways for the motor fuel island equipment shall be rated NEMA 4X.

All outlet and device boxes will be steel for the Office and Bay Areas and will be concealed, including boxes for temperature sensors associated with BAS system.

Underground Ducts and Raceways for Electrical System:

Typically the minimum underground raceway size is 1”. The exception is the motor fuel island, generator diesel monitoring, and tank monitoring system conduits are typically ¾” in size. Raceways shall be PVC schedule 40 when installed underground in grass areas. Raceways will be PVC schedule 80 when installed underground in paved areas. All sweeps and stub-ups will be RGSC. All sweeps and stub-ups in corrosive areas, walkways and pavement will be PVC coated RGSC. Conduits routed from the exterior to the interior of a new construction building shall sweep up on the interior of the building.

Where electrical capacity is reserved for future use, the Electrical Designer shall provide spare underground conduits to an accessible point.  The number and size of conduits shall be appropriate to the equipment.

Overcurrent Protective Device (Short-Circuit Study and Arc-Flash Study):

The Contract will require the Contractor to hire a company to perform the study and label the electrical panels accordingly.

Lighting Control Devices:

Photocells will be mounted on the exterior of the building above the roof line without penetrating the roof. Photo eye will face north. All exterior lighting will be controlled by the photocell except for the motor fuel island and storage yard lighting that will be controlled by local switches.  Photocells will be solid state with dry contacts rated for 1800VA to operate connected load, relay, or contact coils. Exterior lighting shall be equipped with pole/fixture mounted occupancy sensor.  Exterior lighting fixtures shall be provided with occupancy sensors capable dimming the fixtures 50% when there is no occupancy. Pole mounted fixture located at the entry shall not be provided with occupancy sensor/dimming capability.

Occupancy sensors will be provided on interior lights as described below:

- Office occupancy sensors will be the dual-technology type (Infrared and ultrasonic). Switch mounted occupancy sensor shall be installed where practical.

- Bathroom occupancy sensors will be the ultrasonic type.

- Bay occupancy sensors will be the infrared type.

- Occupancy sensors shall not be installed in service rooms and hallways.

Occupancy sensors will be equipped with time delay function and with an override switch.  Occupancy sensor power packs will be as required. Occupancy sensor voltage will be 24V DC.  Ultrasonic and dual-technology occupancy sensors will be installed at least 6 feet away from HVAC supply/return vents.

Occupancy sensor and dimming devices will be wet location rated where required.

In Office Areas along the windows, provide switching for lighting fixtures located within 15 ft. of the windows, or provide daylight harvesting control system for lighting fixtures within this area.

Lighting contactors will be digital except for those installed in salt sheds which will be electrically operated and mechanically held.  The lighting contactor will be equipped with a two position type switch designated as “Manual” and “Auto”.

Panelboards and Switchboards

All bussing in electrical power distribution system components shall be copper. Design switchboards, switchgear, and motor control centers with 15%-25% space for additional overcurrent protective devices.  Design panelboards with 15%-25% space for additional circuit breakers.

All circuit breakers shall be the bolt-on type. The interrupting capacity of electrical equipment shall be equal to or greater than the available short-circuit current as its supply terminal.

Panelboards and equipment shall be mounted on ¾” fire retardant plywood treated on all sides and painted with two coats of enamel paint. Fire retardant plywood shall be installed in all Electrical Room and Communications Room walls from 2’ to 8’ AFF. Specify for the Contractor to balance the electrical loads and maintain 20 percent between phase loads within each panelboard during installation or maintaining panelboard layout according to the Contract plans.

Motor-Control Centers

Provide quick-make, quick-break, toggle switch type, with thermal alloy type overload protection. Use manual motor starter for single-phase motors rated less than ½ horsepower. Motors rated 1/2 HP and higher shall be 3-phase. Provide switch with a red indicating light to show when the switch is in the closed position.

Provide combination magnetic controller for all three phase motors that require a starter. The controller will have full voltage across the line, equipped with magnetic starter and motor circuit protector, sized to conform to the NEMA standard. Specify a control transformer for 120 volt control. Specify three thermal type ambient compensated manual reset overload relays based on the actual motor type. Specify one additional auxiliary interlock contact. Specify red and green pilot lights, start-stop pushbutton, and Hand-off-auto selector switch. All starter selector switches will be key-operated in the bays except for the ones installed in the service rooms.

Electricity Metering

Design shall investigate potential rebates offered by the local electric company for the use of energy saving equipment.

The Designer shall prepare and submit load calculations that justify the size of the service and the size of each branch circuit and feeder, overcurrent protective device, transformer, and equipment bus (panelboard, switchboard, switchgear, automatic transfer switch, etc.).  The method of calculation shall be clearly presented in the drawings, including all applicable NEC diversity factors and non-coincident loads and their employment at various levels of the electrical system, as well as the capacity reserved for future load.  Calculations may be included in panel schedule and switchboard schedule format.

Utility conduits will be equipped with expansion couplings per local utility requirements. Service size shall be design for future expansion.

From the utility coordination meeting a site plan is developed and sent to the utility company for further review.  All coordination information is included within the specifications and plans.

Wiring Devices:

Tumbler-toggle switches will be heavy duty. Switches will be side wired and equipped with holes for back wiring. Switches used for controlling motors will be rated for at least the horsepower of the motor controlled.

Receptacles will be the duplex type, configuration 5-20R. Receptacles will be side wired and equipped with holes for back wiring.  Ground fault interrupter receptacle will be the duplex type; configuration will be 5-20R and equipped with pilot light to indicate if receptacle is working or tripped.  GFCI receptacles will be installed in all the Bays, Mechanical Rooms, Sprinkler Rooms, Electrical Rooms, Communications Rooms, Kitchenette areas, exterior of the building, and as required by code.  Block heater receptacles will be controlled from the Building Automation System and shall be equipped with a GFI circuit breaker.  Receptacles and block heater receptacles will be provided in sufficient quantities to avoid the excessive need to use extension cords.  Quad box receptacles will be installed at workbenches to eliminate the need for power strips.

Coordinate requirements with kitchenette equipment list.  Provide appropriate receptacles for each cord-connected piece of kitchen equipment.

Cord reels will be industrial grade, configuration 5-20R, 35ft in length or as required. Cable type will be 12/3 SOW-A.  Cord reels are typically provided in Repair facilities. Cord Reels shall be connecter to GFI circuit breakers.

Calcium Chloride/Magnesium Chloride receptacle and plug will be 3 phase, Watertight 250Volt, 30Amp, 3 Horsepower rated, configuration NEMA L15-30R and NEMA L15-30P, respectively.

Welding receptacles and other specialty equipment shall match existing or equipment to be installed.  Receptacles will be installed where requested by the owner/occupant.

Power washer receptacle will be Watertight 250V, three phase, 30 amperes, 3-pole, 4 wire grounding NEMA L17-30R.

Device plates for wall outlets, switches, and wall telephone outlets will be satin finish stainless steel.  Device plates for wall telephone outlets will have two openings for RJ45 jacks: (1) for voice and (1) for data.  Device plates for wet locations will be gasketed and will be equipped with heavy duty in-use type covers.  PVC weatherproof covers will be provided for all switches in the Salt Shed.

Call for Aid System will be installed in single occupancy bathrooms or at other locations where a privacy latch set is installed on the bathroom door.  The horn and strobe will be designed for a single gang box located over the door. The pull cord station will provide emergency call activation and reset. It will have a stainless steel face plate with DPST switch.

For security reasons, the inner vestibule door will be locked when the facility is occupied.  The Architect will specify an electric strike for this door.  Install a door strike release pushbutton inside the Clerk’s Office, convenient to the Clerk’s desk.  If there is no visitor check-in window between the Clerks’s Office and the Vestibule, install an intercom system

Grinder pump station alarms, fire pump alarms, Building Automation System alarms will be installed in the Clerk’s office.

Contractor will insulate behind door operator push buttons when mounted on columns.

Install emergency shut off switches for the boilers and water heater at the entrance of the Mechanical Room.

Enclosed Switches and Circuit Breakers

Disconnect switches will be the heavy duty type with lockable handle. Fusing will be as required for the application. Main circuit breakers enclosures shall be equipped with lockable handles.

Fuel island Disconnect: A low voltage dispenser disconnect will be suitable for flammable liquid dispensing devices. Low voltage dispenser disconnect is designed to function as a disconnect for low voltage dispensing devise wiring. This product is intended to be used at fueling sites to provide compliance to the NEC Section 514.11 and 514.13.

Generator:

The Designer shall prepare and submit calculations that justify the size of the generator, including but not limited to all loads downstream of the generator set and the sizing impacts of proposed load, significant motor loads, non-linear loads, and capacity reserved for future loads.  If applicable under NEC Article 517, prudent demand factors and historical data used to justify generator set sizing shall be clearly presented.

The engine generator will be classified as a Type 10, Class 48, Level 2 Standby Power Supply system in accordance with NFPA 110.  The generator ampacity shall be sized to handle 100% of the calculated load of the site. Typically a diesel generator is used. The tank will be the double-wall construction type. The fuel tank will provide sufficient fuel for 48 hours at 75% load.  Where natural gas is available, a natural gas fueled generator shall be explored.  The fuel tank will be equipped with a 2” port to connect a sensor to the Tank Monitoring System.

The generator will be located on the Project Site to minimize the noise impacts to Department personnel as well as the abutting neighbors.  Siting concerns raised on past projects including locating the generator away from the Conference Room (rest breaks) and other full-time occupied spaces such as offices and Repair areas.

The generator will only be equipped with a weatherproof sound attenuated enclosure, 14 gauge aluminum, gravity-operated louvers, and rain ledges if site constraints/neighbors require it.  Otherwise the generator can be the manufacturer’s standard color. The complete enclosure will be painted color gray. A block heater and battery charger circuit is required sized per manufacturer’s recommendations. The generator will be equipped with a shut-down button in location indicated on the plans.

Automatic Transfer Switch (ATS)

The transfer switch will switch all ungrounded service entrance feeders after the MDS.

The controller will include a 20-character, LCD display, with a keypad, which allows access to the system.

The ATS will be capable of receiving a remote signal from closed contacts of the building automation system to activate the weekly exercise function (“under load exercise sequence”), which will run as long as the contacts are closed. The generator will be capable of providing status information to the building automation system. The ATS will start the generator, transfer, and will close a set of auxiliary contacts that the automation system will monitor to indicate that the “Generator Running and Supplying Load” on the automation system. The load will transfer back to commercial power after an adjustable time upon the opening of automation system signal contacts. The generator will automatically shut down after an adjustable cool down time. The ATS will be able to communicate with any Building Automation System (BAS) such as Trane and Johnson Controls.

A remote annunciator will be installed in the Clerk’s Office to monitor the generator status.  It shall be flush mounted unless it is installed in a fire rated wall.

Lightning Protection for Structures

Lightning protection systems shall comply with NFPA 780 – Standard for the Installation of Lightning Protection Systems and NFPA 70. A certification letter, signed by the Contractor, that the roof adhesive for air terminals is approved by manufacturers of both the terminal assembly and the single-ply membrane roofing material shall be submitted.

Engage an experienced installer who is an NRTL or who is certified by LPI as a Master Installer/Designer. Roof-mounting air terminals will be Class I, copper.

Each down conductor will terminate at a ground terminal dedicated to the lightning protection system. Down conductors will be installed in PVC conduit and will be concealed from the outside of the building. There shall be no exterior surface mounted conduit. All grounding media in or on a structure will be interconnected to provide a common ground potential. This interconnection will include lightning protection, electric service, as well as underground metallic piping systems. The grounding electrode system of the lightning protection system will be bonded to the electrical service grounding electrode system.

Use exothermic-welded connections for all conductor splices and connection between conductors and other components, except those above single-ply membrane roofing. Do not combine Aluminum with Copper materials directly. Use appropriate connectors rated for the application and each material. Obtain a UL Master Label for the system installed. Provide surge protection system as required by UL96a suitable for lighting protection systems. The contractor will provide individual units for the telecommunications and electric systems.

Surge Protection for Low-Voltage Electrical Power Circuits

Surge protector will be mounted on the load side of the main disconnect overcurrent protection. Surge protector will be equipped with a surge counter and will be equipped with internal thermal protection. The Peak surge current rating and modes of protection will be UL 1449 listed per the voltage system. The surge protector will be mounted in an enclosure. The circuit connections will be as short and as straight as possibly (less than 24”). Provide a fused disconnect switch as an OCPD for the voltage suppressor.

LED Interior Lighting:

A complete photometric lighting analysis showing all the illuminance levels, uniformity, lamp loss factor, lamp depreciation, power densities, etc. shall be prepared.  Calculations shall not be a part of the contract documents. CTDOT shall be provided with the calculations for review and comments during the design phase. Illumination levels shall be based on the latest edition of the IESNA Lighting Handbook.

Provide a Lighting Fixture Schedule on the plans, separate from the specifications.  The Lighting Fixture Schedule shall state details such as fixture designations used on the plans, lighting fixture descriptions, exact lamp type, etc.

The Color Rendering Index (CRI) will be a minimum of 90 and the Correlated Color Temperature (CCT) will typically be 4000K.

Wash Bay: Lighting will be wet location rated.

Salt Shed: Lighting will be rated for corrosive location/marine type rating.

Light fixtures located near the overhead doors will be mounted to avoid interference with door operation. Install fixtures to avoid being blocked by the door while door is in the open position in order to provide unblocked light source. Fixtures may be suspended in-between and below door rails and shall not interfere with the door or door operation.

LED task lighting will be installed above work benches and at other locations requested by the facility owner or occupant.

Provide LED angled lighting wall mounted over mirror in the restrooms in addition to standard ceiling mounted LED lighting. A wet location shower light is also required.  Coordination shall be made with the Plumbing Designer because shower lights are typically provided by the shower enclosure supplier.

Emergency and Exit Lighting:

Emergency lighting unit will be installed in the interior to the light fixtures designated to be emergency light fixtures.

Exit signs will be equipped with self-diagnostics and visual indicators.  Exit signs will be powered by the closest interior lighting circuit. Exits signs will be un-switched (wired before the switch).  Exit signs will include the ANSI symbol for accessibility at each accessible exit door.

No exterior emergency lighting is required if the lighting system is a load associated with a standby generator.

Lighting Poles and Standards:

Basic Wind Speed will comply with the Building Code for the project location.  A 1.3 gust factor for total support assembly, including pole, base, and anchorage will be applied. Exterior lighting fixtures shall be provided with occupancy sensors capable dimming the fixtures 50% when there is no occupancy. Pole mounted fixture located at the entry shall not be provided with occupancy sensor/dimming capability.

Poles and arms will be made of aluminum.  Poles, arms, and mount materials will have a bronze finish.  Poles will be equipped with transformer bases. The bases will be made of aluminum, box-type shape used for wiring access and as a breakaway device.  All mounting components will be corrosion-resistant compatible with pole and arms.  Anchor bolts will be galvanized and the type will be the J-type bolt.

Provide complete pole base details on plans. Details shall indicate complete structural and electrical elements such as rebar, type of concrete, anchors, conduits, handholes, etc.

LED Exterior Lighting:

A complete photometric lighting analysis showing all the illuminance levels, uniformity, lamp loss factor, lamp depreciation, power densities, etc. shall be prepared.  Calculations shall not be a part of the contract documents. CTDOT shall be provided with the calculations for review and comments during the design phase. Illumination levels shall be based on the latest edition of the IESNA Lighting Handbook.

Provide a Lighting Fixture Schedule on the plans, separate from the specifications.  The Lighting Fixture Schedule shall state details such as fixture designations used on the plans, lighting fixture descriptions, exact lamp type, etc.

Minimize spill illumination onto adjacent properties (use house-side shields when adjacent to residential property).

All exterior lighting will be the full-cut off type with the exception of flag pole lighting and predator style sand pile lighting.  The Color Rendering Index (CRI) will be a minimum of 90 and the Correlated Color Temperature (CCT) will typically be 4000K.

CSI DIVISION 27 – COMMUNICATIONS

Telecommunication Systems:

Contact CTDOT telecommunications personnel for technical assistance with systems design and preparation of construction documents. Project funding will be made available for IT to purchase and install a phone switch and routers.  The patch panels will be manufactured by Siemon, who is a preferred partner with Cisco (the standard for network hardware), NEC (the standard for phone systems in maintenance facilities) and Avaya (the standard for phone systems in the Headquarters, District Offices, and the Rocky Hill Lab).

Voice/Data communications outlets shall be manufactured by Siemon.  There is a sole-source approval memorandum on file.  Voice/Data communications outlets will terminate at a new patch panel for voice and a new patch panel for data. All final cross connections will be performed by the contractor under the supervision of ConnDOT telecommunications personnel. Layout of the voice/data equipment shall be as shown on the plans. Each outlet will have one voice cable and one data cable. Two RJ45 jacks that together fit a single gang opening with one white receptacle (Telephone) for Category 6 wire and one orange receptacle (Data) for Category 6 wire will be installed. All cable will be Category 6 yellow except for underground. Each Category 6 cable will be identified on both ends using wire tags. The cable will have 18” excess length on the communication outlet side and 36” excess at the terminal board side. Label all communication outlets and patch panels. Handwritten labels are not acceptable. The largest patch panel allowed is a forty-eight port panel. Spare capacity required of 20 percent is required.

The maximum cable length from the Data Room to the most remote communication outlet (inside the building and outside the building to the FMU) is 300-feet.

A letter of certification stating compliance with EIA/TIA-568 will be furnished along with a written report showing test results on all tested parameters.

Supply infrastructure (Conduit and patch panels) from telecommunications room or secondary communications closet to the offices and to the repair bays for wireless access points.

Install two RJ31X telephone receptacles in the proximity of the dialer for the fire alarm dedicated phone lines.

Additional voice/data requirements:

- If a fuel island is present at the facility, a network connection for Fuelmaster and the tank monitoring system will be required. Mount and make necessary connections required for the network communication system. The Contractor will contact Mr. Denis Richard from CTDOT telecommunications a week prior to the installation of the communication jacks for the Fuel Island.

- CTDOT telecommunications will provide direction on the installation of telephone line from the data panel as well as the location of the line seizure relay required for the Fuel Island.

- A dial up line is required for the building automation system (BAS).

- The Contractor shall contract with the Department’s Security Monitoring vendor, Johnson Controls Security (formerly known as ADT/Tyco) and have the following items installed and connected to monitor the fire alarm panel and report to the Johnson Control Security Central station: (1) digital dialer with 4G cell backup to monitor 2 points - Fire Alarm and Fire Trouble.  The Department will ONLY be responsible to supply dial tone at the telco demark. The Contractor is responsible to bring via conduit a cat 6 cable to the dialer, to provide and terminate RJ31x at the dialer, and also to provide line power to the dialer/communicator.  If a plug in transformer is used it must be enclosed in an electrical box or under a NFPA compliant protective cover.  The contractor shall be responsible for all programing of fire panel to give Johnson these 2 outputs of Fire Alarm and Fire Trouble.  The contractor is responsible for all costs associated with this work.

- Voice/data outlets are required at the Stores service window and at the Stockroom workbench by the exterior Stockroom door.

Coaxial cable and outlets for Cable TV will be installed in each Break Room and Conference Room, wired from the Communications Room.

Base Station Radio System:

The basis-of-design for the 45-foot tall antenna tower is Rohn Model 65G.  The antenna tower load will be designed to the Building Code for the basic wind speed along with ½ inch ice rating.  The design will include a geotechnical boring for the Contractor to design the foundation.  If a boring is not included in the design, the Contractor shall perform the boring.  An overhead bridge structure will be constructed from the tower to the building so that the antenna cable does not need to be installed underground.  The antenna cable will run continuously without splices.   The basis-of-design for the antenna shall be Commander Technologies Model: 1142-2CN at 47.24 Megahertz Female N-type connection or Kreco Antennas Model:  CO-36A at 47.12 Megahertz Female N-type connection.

The base station radio antenna system will be included in projects when required by the Department’s Rocky Hill Radio Lab (reports to Maintenance).  The system will be designed to their requirements, including the antenna frequency (47.12 MHz).

In addition to the antenna tower and cable infrastructure, the base station radio system shall include all the necessary radio components for an operable system including but not limited to the low band radio, tone remote(s), grounding, power supplies, adapters, mounting of equipment, and installation. The radio equipment, antenna and cables shall be installed by the contractor and inspected by the DOT Radio Communications supervisor.

Public Address System:

Each employee group (Repair, Maintenance, Electrical, etc.) within the building needs local paging capabilities along with overall paging capability for the entire building.  PA desktop equipment will be installed in the Clerk’s Offices unless otherwise directed. Remote microphone shall be provided in other areas as required.  Speakers located in the Conference Room will be equipped with on-off switches and volume control.  The design will require 18 inches excess cable at each termination point. The system shall be capable of future connection to the telephone system.

Intercoms between Vestibules and Clerk Offices will be provided if there is no line of sight between the 2 spaces.

Stores facilities require a communication system (intercom or doorbell) between the Repair Bay service window, the Stores Office, the Stockroom, and the exterior Stockroom door to be alerted to requests for service or deliveries.  Tones shall be different to distinguish between the service window and the exterior Stockroom door.

Training Infrastructure

Each Conference Room will include clear wall space for a flat screen TV.  A junction box will need to be installed __” AFF for each TV.  A junction box will be installed __” AFF in the area of the future computer.  Conduit and an HDMI cable will need to be installed between these (2) boxes.

A junction box of the appropriate size will be installed __” AFF for the Crestron controller.  A junction box will be installed __” AFF in the area of the future computer.  Conduit and an HDMI cable will need to be installed between these (2) boxes.

A power receptacle will be installed __” AFF in the area of the future computer.

The training equipment will be installed by DOT IT.

CSI DIVISION 28 – ELECTRONIC SAFETY AND SECURITY

Video Surveillance System:

Typically the only video surveillance system includes cameras on or pointed towards the fuel island with the video surveillance monitor installed in the Clerk’s Office only if the Clerk’s Office does not have direct line-of-sight visibility of the motor fuel island.  Provide high definition, digital, IP, color cameras, fixed mounted, suitable for exterior applications. The camera shall be connected to the data infrastructure of the building. The cameras shall not be connected to the onsite network but should have capabilities to do so in the future. Provide a Network Video Recording (NVR) suitable to accept connection from the camera. Provide color, LCD monitor, 24” minimum connected to the NVR. Video monitor bracket shall be installed 5’-6” AFF measured to the center of bracket. Video surveillance monitor receptacle to be mounted at 4’-6” AFF.

Fire Alarm System:

Notifier shall be the basis-of-design for the addressable fire alarm system.  The fire alarm control panel shall be installed in the Electrical Room with a remote annunciator installed in the Office Area Entry Vestibule. Fire alarm system shall be FM Global approved and shall be installed in accordance to the FM Global Data Sheets 5-40 and 5-48. Central panel shall contain a dialer to alert local fire authorities in the event of alarm activation. The system shall contain Class ‘A’ independently supervised initiating circuits The fire alarm system shall be equipped with battery back-up.  Install a ¾” conduit with pull string from a junction box next to the dialer to the closest point outside not to exceed 90 feet (but not on the roof).  This is to avoid a potential change order if the cellular service signal strength is not acceptable.

Wiring for the fire alarm systems shall be installed in conduit throughout the building. Fire Alarm conduit and junction boxes shall be only for the fire alarm system. All boxes shall be painted red.

Heat detectors shall be mounted on the ceiling.  Early detection low heat (135 deg. F) heat detectors shall be installed in the Break Rooms, Bathrooms, Locker Rooms, and Mechanical Rooms regardless of whether or not a sprinkler system is installed.  If there is no sprinkler system, 194 deg. F heat detectors shall be installed in the Bays.

Smoke detectors shall be mounted on the ceiling whether or not a sprinkler system is installed.  Smoke detectors are required per 2015 IRC Section R314, with particular note to R314.3 (Location) and as amended by the 2018 CT Supplement. In general, smoke detectors are required within any rest break area and just outside of them. Consult with the Project Engineer and the Architect but the intent of the typical project is to permit employees to rest in any location within any office, Conference Room, or Break Room.  This is also required under the 2018 CT Supplement to the 2015 IBC Section 907.2.8.2 Automatic Smoke Detection System.  Additionally, smoke detectors shall be installed in all closets/storage rooms, Janitor’s Closets, Electrical Rooms, and Data Rooms.

Duct smoke detectors are to be installed where required. Provide a remote indicating lamp and a test key switch on nearby wall to facilitate testing, mounted at 48” centered to the test station.

Fire alarm strobes shall be supplied for all Office Areas. Fire alarm strobe/horn combination devices shall be supplied for all Bathrooms, Mechanical Rooms, Sprinkler Rooms, Electrical Rooms, Communications Rooms, Bay Areas, Hallways, Basements, Conference Rooms, and exterior to the building. The Conference Room horn should be selected based on the room’s use for resting.  Wash Bays and exterior devices shall be weatherproof. Mounting of strobes and horn/strobes shall be at 7’-6” centered to the device. In addition to the wall mounted horn/strobes, ceiling mounted horn/strobes shall be provided in the Bay Areas to prevent a truck from blocking the strobe/horn device on the walls.

Fire alarm pull stations shall be mounted at 48” centered to the device at exit doors.

Fire alarm system shall monitor all fire suppression systems installed; the Designer shall coordinate with the Mechanical/Fire Protection Designer.

Carbon Monoxide detection is exempt in accordance with the 2015 IBC 915.1.4 Exception 1.

SALT SHEDS AND PERSONNEL SHELTERS

Salt Sheds:

The Department has standard salt shed designs for operational sheds and for reserve sheds.

Personnel Shelters:

Salt Sheds located on sites without maintenance facilities require a personnel shelter to offer a place for the Payloader operator to take a break from loading salt into plow trucks during winter storms.

The historical design for a personnel shelter was a 12 foot square wood framed insulated building with high-abuse interior wall covering, counter to be used as a writing surface, and a window.  Electric heat on a 6 hour timer will be installed for heat.  Power and communications to the personnel shelter shall be underground.  A telephone outlet will is required above the counter with the cable terminating outside next to the service conduit.  The telephone company will then make the final connections.  A 110V/battery backup smoke detector is required.  Refer to the plans and specifications for the most recent (Fairfield Salt Shed) for the current personnel shelter design requirements.

An optional personnel shelter design for consideration, though as of this writing not designed or constructed, is based on Staff Maintenance’s 8 foot by 20 foot rest break trailer.

SALT SHED REHABILITATION PROJECTS TYPICAL SCOPE OF WORK

Roofing:

Remove the existing asphalt shingle roof and install a PVC extrusion roof system including an end of roof water shield to divert water runoff away from the existing concrete pilasters, a roof cover board, plywood sheathing at the roof transition and perimeter, vapor retarder, and a snow retention system. Add additional fasteners and/or blocking at the existing plywood substrate where required for the installation of the roof cover board.  Replace the existing plywood substrate as required for a proper roof installation.

Additional Building Improvements as Required on a Project-Specific Basis:

Trim Work at the roof’s edge, louvers, and wall below the soffit: Add additional fasteners as required.  Paint or stain.

Remove mega door and hardware at the entrance of the salt shed.

Replace the existing front and rear louvers, trim and bird screens that are damaged or missing. Paint or stain existing and replacement louvers and trim.

Install (2) of 5’- 0” wide by 6’- 6” high wood louvers with a 1” x 4” trim within the rear wall.

Center louvers horizontally and spaced approximately 7’-8” apart from outside of trim to outside of trim as it relates to interior wall framing.  Louvers shall be located vertically at 7’- 0” from top of existing concrete pilaster to bottom of louver trim.

Remove canopy over the door.  Install plywood sheathing, underlayment and cedar shakes to match the existing walls.

Remove the personnel door at the front of the salt shed and retrofit this area with framing, sheathing, underlayment, and cedar shakes to match existing.

Replace broken or damaged cedar shakes as required, typically to the extent of shakes that are available at the shed due to selective demolition.

All existing and installed cedar shingles shall be stained.

Apply joint sealant at gaps around all wood trusses and laminated arch framing at interior barrier wall ledge.

Caulk joints at underside of plywood soffit where it abuts the existing wall, pilasters and water shield.

Work Typically Excluded:

The typical salt shed roof rehabilitation project does not repair any concrete.

APPENDIX

1 – Electrical/Communications Room Design Criteria

2 – Office Furniture

3 – Break Trailer Floor Plans

4 – Typical Vehicle Dimensions and Block Heater Requirements

Appendix 1

Appendix 2 – 1	Office Furniture

Offices

Clerk

72 W x 36 D Tabletop	1

24 D x 36 W Tabletop	1

23 D x 15 W Pedestal File	2

24 W x 66 H Storage Cabinet	1

18 D x 42 W Filing Cabinet	2

36 W x 14 H Overhead Cabinet (opt.)	1

Computer Chair	1

Keyboard Tray	1

Crew Leader

30 D x 48 W Tabletop w/ Pedestal File	1/person

24 W x 66 H Storage Cabinet	1/person

18 D x 42 W Filing Cabinet	1/person

Computer Chair	1/person

Chair	1/person

Supervisor

48 D x 72 L Tabletop	1

24 D x 42 W Tabletop	1

24 D x 72 W Tabletop	1

23 D x 15 W Pedestal File	2

36 W x 14 H Overhead Cabinet (opt.)	1

30 W x 14 H Overhead Cabinet (opt.)	1

24 W x 66 H Storage Cabinet	1

18 D x 42 W Filing Cabinet	1

Computer Chair	1

Keyboard Tray	1

Chairs	2

The following plan views are based on the Milford Repair and Maintenance Facility.

They are included for reference.

Appendix 2 – 2	Office Furniture

Appendix 3 – 1	Break Trailer Floor Plans

Appendix 3 – 2	Break Trailer Floor Plans

4 – Typical Vehicle Dimensions and Block Heater Requirements

| Vehicle | Length | Width | Height | Block Heater Required? |
| --- | --- | --- | --- | --- |
| ¾-ton Pickup (diesel) | 21' | 7' |  | Yes |
| ¾-ton Pickup (gasoline) | 21' | 7' |  | No |
| 9-ton single axel w/ single plow | 30' | 10' |  | Yes |
| 9-ton w/ single wing (wing down) | 30' | 18' |  | Yes |
| Boom Truck | 32' | 10'-5" | 12'-7" | Yes |
| Bucket Truck | 27' | 10' | 12'-3" | Yes |
| CBYD Pickup | 18' | 7' | 6' | No |
| Centerline Machine | 34' |  |  | Yes |
| Chippers | 17' | 8' |  | Yes |
| Crash Unit Truck | 27' | 10'-6" | 11' | Yes |
| Crew Leader's Pickup | 18' | 8' | 7' | No |
| Electronics Transport Van | 20' | 8' | 8' | No |
| Elliott (Bridge) | 38' | 8'-6" | 13'-2" | Yes |
| Flail Mowers | 15' | 9' |  | No |
| Guiderail Trailer | 40' | 12' |  | No |
| Hybrid Bucket Truck | 31' | 10'-6" | 12'-2" | Yes |
| New Bucket Truck | 30' | 10'-6" | 12'-7" | Yes |
| Loop Inspector | 20' | 8' | 7'-8" | Yes |
| Loop Truck | 29'-8" | 10'-10" | 11' | Yes |
| Mason Dump | 26' | 9' |  | No |
| Oshkosh Snow Blower | 30' | 10' |  | Yes |
| Over-the-Fence Mower | 15' | 9' |  | Yes |
| Payloader (add 4’ L for snow blower attachment) | 22' - 26' | 9' |  | Yes |
| Quad Cab Pickup | 21' | 7' |  | No |
| Rack Body | 21' | 10' | 7'-4" | Yes |
| Snooper (Bridge) | 41' |  | 13'-6" | Yes |
| Sweeper | 22' | 9' |  | Yes |
| Ten Wheeler w/1 wing plow (wings down) | 35' | 17'-2" |  | Yes |
| Ten Wheeler w/2 wing plows (wings down) | 35' | 22' |  | Yes |
| Tractor Trailer (1) | 53' - 65' | 10' |  | Yes |
| Tree Bucket Truck | 32' | 10' |  | Yes |
| Triaxle w/ wings (wings down) | 40' | 18' |  | Yes |
| Triaxle without plow (17’-4” dump body) | 32’ |  |  | Yes |
| Utility Trailer (for Mason Dump) | 20' | 10' |  | No |

- Only design for tractor trailer if there is one on site or it is known that one passes through consistently.

- If there are any hybrid vehicles on site, a plug needs to be provided for them during design.